## 2024 (hidden)
Location | Feeder Name | Type of risk | Year Identified | Rating (Amps) | 22/23 - 23/24 Load (11kV amps) | 24/25 Load at Risk (11kV Amps) | 25/26 Load at Risk (11kV Amps) | 26/27 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution
Speers Point | ARGENTON 132/11 PA11 | N-1 | 2024 | 400 | 287.0276 | 195.3855 | 195.3855 | 195.3855 | Existing | Under investigation
Copocabana | AVOCA PA24 | N-1 | 2024 | 280 | 166.7642 | 83.6053 | 83.9398 | 84.2755 | Existing | Under investigation
MacMasters Beach | AVOCA PA33 | N-1 | 2024 | 325 | 197.5517 | 58.0794 | 58.3117 | 58.5449 | Existing | Under investigation
Kincumber | AVOCA PA40 | N-1 | 2024 | 400 | 167.2723 | 63.2677 | 63.5207 | 63.7748 | Existing | Under investigation
Bankstown | BANKSTOWN PA14 | N-1 | 2024 | 400 | 273.3989 | 103.1475 | 103.1475 | 103.1475 | Existing | Under investigation
Blakehurst | BLAKEHURST PA01 | N-1 | 2024 | 355 | 253.1458 | 89.825 | 91.9808 | 94.1883 | Existing | Under investigation
South Hurstville | BLAKEHURST PA08 | N-1 | 2024 | 300 | 226.9032 | 37.4512 | 38.35 | 39.2704 | Existing | Under investigation
East Branxton | BRANXTON 66 PA13 | N-1 | 2024 | 400 | 141.1265 | 87.2204 | 87.2204 | 87.2204 | Existing | Under investigation
Burwood | BURWOOD PA09 | N-1 | 2024 | 390 | 250.9616 | 113.5148 | 113.5148 | 113.5148 | Existing | Under investigation
Ultimo | CAMPERDOWN PA69 | N-1 | 2024 | 400 | 151.6184 | 39.0033 | 39.0033 | 39.0033 | Existing | Under investigation
Campsie | CAMPSIE PA17 | N-1 | 2024 | 165 | 128.3836 | 73.7861 | 74.0812 | 74.3775 | Existing | Under investigation
Belfield | CAMPSIE PA26 | N-1 | 2024 | 210 | 170.8818 | 102.7866 | 103.1977 | 103.6105 | Existing | Under investigation
Campsie | CAMPSIE PA28 | N-1 | 2024 | 355 | 232.1634 | 97.071 | 97.4593 | 97.8491 | Existing | Under investigation
Canterbury | CAMPSIE PA36 | N-1 | 2024 | 230 | 170.9484 | 58.7767 | 59.0118 | 59.2478 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA02 | N-1 | 2024 | 324 | 293.2111 | 274.7511 | 277.4986 | 280.2736 | Existing | Under investigation
Mount View | CESSNOCK SOUTH PA03 | N-1 | 2024 | 400 | 331.0719 | 112.9748 | 114.1045 | 115.2456 | Existing | Under investigation
Kitchener | CESSNOCK SOUTH PA11 | N-1 | 2024 | 249 | 167.4321 | 68.5773 | 69.2631 | 69.9557 | Existing | Under investigation
Charmhaven | CHARMHAVEN PA01 | N-1 | 2024 | 355 | 270 | 31 | 31 | 31 | 2025 | Project in delivery
Kanwal | CHARMHAVEN PA09 | N-1 | 2024 | 305 | 148.1155 | 91.3653 | 91.3653 | 91.3653 | Existing | Under investigation
Breakfast Point | CONCORD PA04 | N-1 | 2024 | 320 | 251.184 | 170.8043 | 170.8043 | 170.8043 | Existing | Project in delivery
Breakfast Point | CONCORD PA18 | N-1 | 2024 | 315 | 232.6013 | 151.3946 | 151.3946 | 151.3946 | Existing | Project in delivery
Breakfast Point | CONCORD PA22 | N-1 | 2024 | 315 | 218.1218 | 145.7248 | 145.7248 | 145.7248 | Existing | Project in delivery
Carringbah South | CRONULLA PA08 | N-1 | 2024 | 340 | 243.2569 | 24.4248 | 25.1575 | 25.9122 | Existing | Under investigation
Cronulla | CRONULLA PA17 | N-1 | 2024 | 340 | 191.9735 | 33.0257 | 34.0165 | 35.0369 | Existing | Under investigation
Croudace Bay | CROUDACE BAY 33/11 PA02 | N-1 | 2024 | 371 | 99.9035 | 76.8938 | 76.8938 | 76.8938 | Existing | Under investigation
Valentine | CROUDACE BAY 33/11 PA12 | N-1 | 2024 | 376 | 246.2073 | 49.4022 | 49.4022 | 49.4022 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA01 | N-1 | 2024 | 300 | 283.6684 | 205.3192 | 205.3192 | 205.3192 | Existing | Under investigation
Edgeworth | EDGEWORTH 33 PA04 | N-1 | 2024 | 330 | 188.0555 | 69.8596 | 69.8596 | 69.8596 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA09 | N-1 | 2024 | 315 | 194.8026 | 194.8026 | 194.8026 | 194.8026 | Existing | Under investigation
Holmesville | EDGEWORTH 33 PA10 | N-1 | 2024 | 400 | 368.5771 | 157.9942 | 157.9942 | 157.9942 | Existing | Under investigation
Empire Bay | EMPIRE BAY PA04 | N-1 | 2024 | 400 | 158.5172 | 20.6089 | 21.021 | 21.4415 | Existing | Under investigation
Kilcare | EMPIRE BAY PA08 | N-1 | 2024 | 400 | 154.8957 | 93.4151 | 95.657 | 97.9528 | Existing | Under investigation
Riverview | HUNTERS HILL PA41 | N-1 | 2024 | 330 | 150.8837 | 51.601 | 51.601 | 51.601 | Existing | Under investigation
Adamstown Heights | KOTARA 33 PA03 | N-1 | 2024 | 371 | 164.5158 | 24.687 | 24.687 | 24.687 | Existing | Under investigation
Kurri Kurri | KURRI 132/11kV PA06 | N-1 | 2024 | 400 | 221.6058 | 49.2028 | 49.2028 | 49.2028 | Existing | Project in delivery
Gillieston Heights | KURRI 132/11kV PA19 | N-1 | 2024 | 400 | 282.5971 | 240.3148 | 240.3148 | 240.3148 | Existing | Project in delivery
Summerland Point | LAKE MUNMORAH PA07 | N-1 | 2024 | 390 | 260.5885 | 141.4053 | 143.1022 | 144.8194 | Existing | Under investigation
Lake Munmorah | LAKE MUNMORAH PA10 | N-1 | 2024 | 370 | 115.9397 | 23.8442 | 24.1303 | 24.4199 | Existing | Under investigation
Lake Munmorah | LAKE MUNMORAH PA11 | N-1 | 2024 | 400 | 269.4575 | 62.0102 | 62.7543 | 63.5074 | Existing | Under investigation
Narara | LISAROW PA03 | N-1 | 2024 | 305 | 221.8015 | 32.6985 | 32.7639 | 32.8294 | Existing | Under investigation
Wyoming | LISAROW PA11 | N-1 | 2024 | 325 | 174.8659 | 20.9012 | 20.943 | 20.9849 | Existing | Under investigation
Bateau Bay | LONG JETTY PA02 | N-1 | 2024 | 280 | 216.8677 | 94.1842 | 96.7272 | 99.3388 | Existing | Under investigation
Bateau Bay | LONG JETTY PA10 | N-1 | 2024 | 320 | 286.9518 | 142.1185 | 145.9557 | 149.8965 | Existing | Under investigation
Bateau Bay | LONG JETTY PA18 | N-1 | 2024 | 320 | 189.9476 | 101.3789 | 104.1161 | 106.9273 | Existing | Under investigation
Toowoon Bay | LONG JETTY PA22 | N-1 | 2024 | 370 | 145.6768 | 73.4221 | 75.4045 | 77.4404 | Existing | Under investigation
The Entrance | LONG JETTY PA25 | N-1 | 2024 | 400 | 150.3288 | 40.7321 | 41.8319 | 42.9613 | Existing | Under investigation
Aberglassyn | MAITLAND 33 PA04 | N-1 | 2024 | 260 | 245.6296 | 245.6296 | 245.6296 | 245.6296 | Existing | Under investigation
Aberglassyn | MAITLAND 33 PA07 | N-1 | 2024 | 290 | 335.9507 | 281.7451 | 281.7451 | 281.7451 | Existing | Under investigation
Largs | MAITLAND 33 PA11 | N-1 | 2024 | 260 | 278.6722 | 262.3766 | 262.3766 | 262.3766 | Existing | Under investigation
Bolwarra | MAITLAND 33 PA13 | N-1 | 2024 | 260 | 243.3706 | 181.775 | 181.775 | 181.775 | Existing | Under investigation
Fletcher | MARYLAND 132 PA02 | N-1 | 2024 | 330 | 249.2001 | 209.4897 | 209.4897 | 209.4897 | Existing | Under investigation
Fletcher | MARYLAND 132 PA06 | N-1 | 2024 | 400 | 292.7083 | 224.5017 | 224.5017 | 224.5017 | Existing | Under investigation
Cameron Park | MARYLAND 132 PA10 | N-1 | 2024 | 400 | 81.11 | 54.9968 | 54.9968 | 54.9968 | Existing | Under investigation
Mascot | MASCOT PA25 | N-1 | 2024 | 255 | 157.2835 | 35.6736 | 35.6736 | 35.6736 | Existing | Under investigation
Matraville | MATRAVILLE PA15 | N-1 | 2024 | 300 | 217.4373 | 66.5242 | 68.3869 | 70.3018 | Existing | Under investigation
Eastwood | MEADOWBANK PA31 | N-1 | 2024 | 390 | 324.3336 | 88.6493 | 89.0925 | 89.538 | Existing | Under investigation
Medowie | MEDOWIE 33 PA02 | N-1 | 2024 | 315 | 204.2176 | 121.2624 | 124.6578 | 128.1482 | Existing | Under investigation
Medowie | MEDOWIE 33 PA04 | N-1 | 2024 | 315 | 263.9367 | 140.5515 | 144.4869 | 148.5326 | Existing | Under investigation
Gilleston Heights | METFORD 33 PA10 | N-1 | 2024 | 315 | 266.1785 | 231.3064 | 231.3064 | 231.3064 | Existing | Project in delivery
Muswellbrook | MITCHELL LINE 66 PA11 | N-1 | 2024 | 332 | 135.5696 | 97.1657 | 97.1657 | 97.1657 | Existing | Under investigation
Warriewood | MONA VALE PA05 | N-1 | 2024 | 400 | 264.5654 | 170.2095 | 170.2095 | 170.2095 | Existing | Under investigation
Morisset Peninsula | MORISSET 132 PA04 | N-1 | 2024 | 400 | 241.5911 | 115.6461 | 115.6461 | 115.6461 | Existing | Under investigation
Morisset | MORISSET 132 PA06 | N-1 | 2024 | 364 | 212.6642 | 52.5878 | 52.5878 | 52.5878 | Existing | Under investigation
Penthurst | MORTDALE PA02 | N-1 | 2024 | 400 | 144.1056 | 51.8353 | 51.8353 | 51.8353 | Existing | Under investigation
Oatley | MORTDALE PA07 | N-1 | 2024 | 355 | 230.093 | 161.7162 | 161.7162 | 161.7162 | Existing | Under investigation
Northbridge | MOSMAN PA41 | N-1 | 2024 | 315 | 248.8639 | 161.6264 | 161.6264 | 161.6264 | Existing | Under investigation
Soldiers Point | NELSON BAY 33 PA04 | N-1 | 2024 | 376 | 225.3612 | 51.8509 | 51.8509 | 51.8509 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA13 | N-1 | 2024 | 376 | 186.7072 | 88.8 | 88.8 | 88.8 | Existing | Under investigation
Bar Beach | NEWCASTLE CBD 33 PA30 | N-1 | 2024 | 296 | 154.5727 | 76.6334 | 76.6334 | 76.6334 | Existing | Under investigation
Budgewoi | NORAVILLE PA08 | N-1 | 2024 | 305 | 198.6821 | 35.1495 | 36.204 | 37.2901 | Existing | Under investigation
Homebush | OLYMPIC PARK PA06 | N-1 | 2024 | 400 | 203.8798 | 26.749 | 27.0165 | 27.2866 | Existing | Under investigation
Ellalong | PAXTON 33 PA09 | N-1 | 2024 | 240 | 214.7558 | 109.2076 | 109.9721 | 110.7419 | Existing | Under investigation
Peats Ridge | PEATS RIDGE PA08 | N-1 | 2024 | 370 | 174.3697 | 142.7804 | 142.7804 | 142.7804 | Existing | Under investigation
Lakemba | PUNCHBOWL PA04 | N-1 | 2024 | 330 | 238.0417 | 63.1306 | 63.7619 | 64.3996 | Existing | Under investigation
Wangi Wangi | RATHMINES 132 PA10 | N-1 | 2024 | 300 | 191.658 | 191.658 | 194.3412 | 197.062 | Existing | Under investigation
Rose Bay | ROSE BAY PA08 | N-1 | 2024 | 300 | 153.6694 | 105.8834 | 107.154 | 108.4398 | Existing | Under investigation
Rose Bay | ROSE BAY PA27 | N-1 | 2024 | 290 | 151.7016 | 116.9211 | 118.3241 | 119.744 | Existing | Under investigation
Aberglasslyn | RUTHERFORD 33 PA02 | N-1 | 2024 | 350 | 383.9123 | 331.5412 | 331.5412 | 331.5412 | Existing | Under investigation
Rutherford | RUTHERFORD 33 PA03 | N-1 | 2024 | 397 | 312.3708 | 83.1797 | 83.1797 | 83.1797 | Existing | Under investigation
Rutherford | RUTHERFORD 33 PA05 | N-1 | 2024 | 400 | 63.1388 | 35.0408 | 35.0408 | 35.0408 | Existing | Under investigation
Aberglassyn | RUTHERFORD 33 PA09 | N-1 | 2024 | 350 | 165.1022 | 154.0244 | 154.0244 | 154.0244 | Existing | Under investigation
Monterey | SANS SOUCI PA02 | N-1 | 2024 | 285 | 209.7445 | 37.9061 | 38.361 | 38.8213 | Existing | Under investigation
Singleton | SINGLETON 66 PA28 | N-1 | 2024 | 450 | 190.6825 | 163.3767 | 163.3767 | 163.3767 | Existing | Under investigation
Somersby | SOMERSBY PA17 | N-1 | 2024 | 295 | 71.8308 | 32.3876 | 32.3876 | 32.3876 | Existing | Project in delivery
Stratfield South | STRATHFIELD SOUTH PA26 | N-1 | 2024 | 400 | 167.9277 | 79.4715 | 79.4715 | 79.4715 | Existing | Under investigation
Lemon Tree Passage | TANILBA BAY 33 PA12 | N-1 | 2024 | 341 | 211.4062 | 45.255 | 45.617 | 45.9819 | Existing | Under investigation
Gilleston Heights | TELARAH 33 PA07 | N-1 | 2024 | 324 | 257.5807 | 204.7019 | 204.7019 | 204.7019 | Existing | Project in delivery
Aberglassyn | TELARAH 33 PA08 | N-1 | 2024 | 295 | 235.9258 | 140.7805 | 140.7805 | 140.7805 | Existing | Under investigation
Gillieston Heights | TELARAH 33 PA10 | N-1 | 2024 | 315 | 176.7297 | 79.9499 | 79.9499 | 79.9499 | Existing | Project in delivery
Thorinton | THORNTON 33 PA11 | N-1 | 2024 | 359 | 200.729 | 113.329 | 113.329 | 113.329 | Existing | Under investigation
Thorinton | THORNTON 33 PA18 | N-1 | 2024 | 359 | 327.3794 | 93.4652 | 93.4652 | 93.4652 | Existing | Under investigation
Ettalong Beach | UMINA PA08 | N-1 | 2024 | 350 | 117.8631 | 47.0297 | 47.453 | 47.88 | Existing | Under investigation
Umina | UMINA PA13 | N-1 | 2024 | 400 | 250.235 | 100.5159 | 101.4205 | 102.3333 | Existing | Under investigation
Wyoming | WEST GOSFORD PA13 | N-1 | 2024 | 330 | 203.9974 | 90.7516 | 90.7516 | 90.7516 | Existing | Under investigation
Wadalba | WYONG PA01 | N-1 | 2024 | 285 | 249.0087 | 95.2306 | 95.2306 | 95.2306 | Existing | Under investigation
Wyong | WYONG PA05 | N-1 | 2024 | 285 | 180.892 | 69.7443 | 69.7443 | 69.7443 | Existing | Under investigation
Wadalba | WYONG PA10 | N-1 | 2024 | 355 | 233.8205 | 46.9675 | 46.9675 | 46.9675 | Existing | Under investigation
Alison | WYONG PA12 | N-1 | 2024 | 370 | 103.2131 | 66.0172 | 66.0172 | 66.0172 | Existing | Under investigation
Wyongah | WYONG PA16 | N-1 | 2024 | 305 | 215.6804 | 97.145 | 97.145 | 97.145 | Existing | Under investigation

## 2025 DTAPR FINAL
Location | Feeder Name | Type of risk | Year Identified | Rating (Amps) | 2024/25 Load (11kV amps) | 25/26 N-1 Load at Risk (11kV Amps) | 26/27 N-1 Load at Risk (11kV Amps) | 27/28 N-1 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution
Speers Point | ARGENTON 132/11 PA11 | N-1 | 2024 | 400 | 322 | 179 | 179 | 179 | Existing | Under investigation
Macmasters Beach | AVOCA PA24 | N-1 | 2024 | 280 | 158 | 45 | 45 | 45 | Existing | Under investigation
Macmasters Beach | AVOCA PA33 | N-1 | 2024 | 325 | 156 | 21 | 21 | 21 | Existing | Under investigation
Punchbowl | BANKSTOWN PA10 | N-1 | 2025 | 300 | 174 | 50 | 50 | 50 | Existing | Under investigation
Brooklyn / Somersby | BEROWRA PA11 | N-1 | 2025 | 350 | 86 | 32 | 32 | 32 | Existing | Project in delivery
Cowan | BEROWRA PA21 | N-1 | 2025 | 350 | 189 | 104 | 104 | 104 | Existing | Under investigation
Blakehurst | BLAKEHURST PA1 | N-1 | 2025 | 355 | 186 | 156 | 156 | 156 | Existing | Under investigation
Blakehurst | BLAKEHURST PA12 | N-1 | 2025 | 355 | 179 | 90 | 90 | 90 | Existing | Under investigation
Branxton | BRANXTON 66 PA13 | N-1 | 2024 | 400 | 232 | 85 | 85 | 85 | Existing | Project under development
Burwood | BURWOOD PA09 | N-1 | 2025 | 390 | 266 | 53 | 53 | 53 | Existing | Under investigation
Canada Bay | BURWOOD PA19 | N-1 | 2025 | 400 | 158 | 136 | 136 | 136 | Existing | Under investigation
Cardiff | CARDIFF 33 PA01 | N-1 | 2025 | 301 | 236 | 46 | 46 | 46 | Existing | Under investigation
Warners Bay | CARDIFF 33 PA12 | N-1 | 2025 | 301 | 208 | 22 | 22 | 22 | Existing | Under investigation
Cardiff | CARDIFF 33 PA16 | N-1 | 2025 | 301 | 245 | 80 | 80 | 80 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA02 | N-1 | 2024 | 335 | 275 | 180 | 180 | 180 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA07 | N-1 | 2025 | 305 | 203 | 60 | 60 | 60 | Existing | Under investigation
Charlestown | CHARLESTOWN 132 PA08 | N-1 | 2025 | 400 | 384 | 119 | 119 | 119 | Existing | Under investigation
Woongarrah | CHARMHAVEN PA01 | N-1 | 2024 | 355 | 314 | 38 | 38 | 38 | Existing | Project in delivery
Hamlyn Terrace | CHARMHAVEN PA09 | N-1 | 2025 | 305 | 255 | 104 | 104 | 104 | Existing | Project under development
Woongarrah | CHARMHAVEN PA10 | N-1 | 2025 | 315 | 224 | 66 | 66 | 66 | Existing | Project under development
Woongarrah | CHARMHAVEN PA12 | N-1 | 2025 | 370 | 120 | 0 | 72 | 72 | 2026 | Project in delivery
Lane Cove | CHATSWOOD PA37 | N-1 | 2025 | 320 | 164 | 194 | 194 | 194 | Existing | Project under development
Lane Cove | CHATSWOOD PA40 | N-1 | 2025 | 400 | 335 | 110 | 110 | 110 | Existing | Project under development
Breakfast Point | CONCORD PA04 | N-1 | 2024 | 320 | 203 | 119 | 119 | 119 | Existing | Project in delivery
Breakfast Point | CONCORD PA17 | N-1 | 2024 | 305 | 180 | 165 | 165 | 165 | Existing | Project in delivery
Breakfast Point | CONCORD PA18 | N-1 | 2024 | 315 | 185 | 79 | 79 | 79 | Existing | Project in delivery
Breakfast Point | CONCORD PA22 | N-1 | 2024 | 315 | 177 | 135 | 135 | 135 | Existing | Project in delivery
Warners Bay | CROUDANCE BAY PA01 | N-1 | 2025 | 282 | 284 | 196 | 196 | 196 | Existing | Under investigation
Valentine | CROUDANCE BAY PA02 | N-1 | 2025 | 373 | 114 | 69 | 69 | 69 | Existing | Under investigation
Belmont | CROUDANCE BAY PA06 | N-1 | 2025 | 373 | 260 | 104 | 104 | 104 | Existing | Under investigation
Valentine | CROUDANCE BAY PA12 | N-1 | 2025 | 337 | 279 | 206 | 206 | 206 | Existing | Under investigation
Pyrmont | DARLING HARBOUR 132/11kV PA09 | N-1 | 2025 | 400 | 287 | 40 | 40 | 40 | Existing | Project in delivery
Cameron Park | EDGEWORTH 33 PA01 | N-1 | 2024 | 293 | 293 | 51 | 51 | 51 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA07 | N-1 | 2025 | 258 | 216 | 41 | 41 | 41 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA09 | N-1 | 2024 | 263 | 197 | 100 | 100 | 100 | Existing | Under investigation
Holmesville | EDGEWORTH 33 PA10 | N-1 | 2024 | 400 | 359 | 108 | 108 | 108 | Existing | Under investigation
Kilcare | EMPIRE BAY PA08 | N-1 | 2024 | 400 | 176 | 87 | 87 | 87 | Existing | Under investigation
Green Point | ERINA PA01 | N-1 | 2025 | 400 | 195 | 33 | 33 | 33 | Existing | Under investigation
Erina | ERINA PA07 | N-1 | 2025 | 400 | 266 | 123 | 123 | 123 | Existing | Under investigation
Erina | ERINA PA13 | N-1 | 2025 | 280 | 173 | 35 | 35 | 35 | Existing | Under investigation
Homebush | FLEMINGTON PA04 | N-1 | 2025 | 300 | 185 | 175 | 175 | 175 | Existing | Project under development
Putney | HUNTERS HILL PA36 | N-1 | 2025 | 340 | 158 | 50 | 50 | 50 | Existing | Under investigation
Riverview | HUNTERS HILL PA41 | N-1 | 2025 | 330 | 155 | 47 | 47 | 47 | Existing | Under investigation
Riverview | HUNTERS HILL PA57 | N-1 | 2025 | 315 | 159 | 38 | 38 | 38 | Existing | Under investigation
Woronora | JANNALI PA25 | N-1 | 2025 | 315 | 121 | 53 | 53 | 53 | Existing | Under investigation
Kurri Kurri | KURRI 132/11kV PA06 | N-1 | 2024 | 400 | 242 | 162 | 162 | 162 | Existing | Under investigation
Heddon Greta | KURRI 132/11kV PA12 | N-1 | 2025 | 400 | 306 | 50 | 50 | 50 | Existing | Under investigation
Gillieston Heights | KURRI 132/11kV PA19 | N-1 | 2024 | 400 | 329 | 115 | 115 | 115 | Existing | Under investigation
Summerland Point | LAKE MUNMORAH PA07 | N-1 | 2024 | 390 | 382 | 152.3997 | 152 | 152 | Existing | Under investigation
Bateau Bay | LONG JETTY PA02 | N-1 | 2024 | 280 | 176 | 145 | 145 | 145 | Existing | Under investigation
Maitland Vale | MAITLAND 33 PA04 | N & N-1 | 2024 | 270 | 291 | 240 | 240 | 240 | Existing | Project under development
Aberglasslyn | MAITLAND 33 PA07 | N & N-1 | 2024 | 290 | 310 | 249 | 249 | 249 | Existing | Project under development
Largs | MAITLAND 33 PA11 | N & N-1 | 2024 | 260 | 257 | 133 | 133 | 133 | Existing | Project under development
Bolwarra Heights | MAITLAND 33 PA13 | N-1 | 2024 | 260 | 226 | 193 | 193 | 193 | Existing | Project under development
Fletcher | MARYLAND 132 PA02 | N-1 | 2024 | 384 | 238 | 67 | 67 | 67 | Existing | Under investigation
Fletcher | MARYLAND 132 PA06 | N-1 | 2024 | 384 | 290 | 53 | 53 | 53 | Existing | Under investigation
Cameron Park | MARYLAND 132 PA10 | N-1 | 2024 | 400 | 102 | 26 | 26 | 26 | Existing | Under investigation
Muswellbrook | MITCHELL LINE 66 PA11 | N-1 | 2024 | 400 | 199 | 100 | 100 | 100 | Existing | Project under development
Wyee | MORISSET 132 PA06 | N-1 | 2024 | 364 | 251 | 64 | 64 | 64 | Existing | Project under development
Mosman | MOSMAN PA36 | N-1 | 2025 | 350 | 112 | 26 | 26 | 26 | Existing | Under investigation
Eleebana | MT HUTTON PA03 | N-1 | 2025 | 288 | 255 | 53 | 53 | 53 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA03 | N-1 | 2025 | 398 | 163 | 31 | 31 | 31 | Existing | Under investigation
Soldiers Point | NELSON BAY 33 PA04 | N-1 | 2024 | 282 | 232 | 109 | 109 | 109 | Existing | Under investigation
Nelson Bay | NELSON BAY 33 PA05 | N-1 | 2025 | 263 | 211 | 124 | 124 | 124 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA09 | N-1 | 2025 | 385 | 147 | 183 | 183 | 183 | Existing | Under investigation
Bar Beach | NEWCASTLE CBD 33 PA30 | N-1 | 2024 | 265 | 241 | 26 | 26 | 26 | Existing | Under investigation
Cessnock | NULKABA 33 PA05 | N-1 | 2025 | 400 | 277 | 93 | 93 | 93 | Existing | Under investigation
Homebush | OLYMPIC PARK PA06 | N-1 | 2025 | 400 | 184 | 88 | 88 | 88 | Existing | Project under development
Homebush | OLYMPIC PARK PA10 | N-1 | 2025 | 400 | 108 | 121 | 121 | 121 | Existing | Project under development
Blacksmiths | PELICAN 33 PA01 | N-1 | 2025 | 400 | 178 | 46 | 46 | 46 | Existing | Under investigation
Rathmines | RATHMINES 132 PA10 | N-1 | 2024 | 288 | 197 | 180 | 180 | 180 | Existing | Under investigation
Raymond Terrace | RAYMOND TERRACE 33 PA04 | N-1 | 2025 | 308 | 51 | 20 | 20 | 20 | Existing | Under investigation
Rose Bay | ROSE BAY PA13 | N-1 | 2025 | 290 | 195 | 78 | 78 | 78 | Existing | Under investigation
Aberglasslyn | RUTHERFORD 33 PA02 | N & N-1 | 2024 | 350 | 447 | 396 | 396 | 396 | Existing | Project under development
Rutherford | RUTHERFORD 33 PA03 | N-1 | 2024 | 380 | 281 | 36 | 36 | 36 | Existing | Project under development
Rutherford | RUTHERFORD 33 PA09 | N-1 | 2024 | 350 | 161 | 151 | 151 | 151 | Existing | Project under development
Whittingham / Abattoir | SINGLETON 66 PA28 | N-1 | 2024 | 400 | 244 | 145 | 145 | 145 | Existing | Under investigation
Kariong | SOMERSBY PA16 | N-1 | 2025 | 295 | 219 | 32 | 32 | 32 | Existing | Under investigation
Somersby | SOMERSBY PA17 | N-1 | 2024 | 295 | 85 | 63 | 63 | 63 | Existing | Under investigation
Redfern | ST. PETERS PA20 | N-1 | 2025 | 400 | 212 | 28 | 28 | 28 | Existing | Under investigation
Erskineville | ST. PETERS PA32 | N-1 | 2025 | 316 | 197 | 45 | 45 | 45 | Existing | Under investigation
Tanilba Bay | TANILBA BAY 33 PA15 | N-1 | 2025 | 337 | 176 | 100 | 100 | 100 | Existing | Under investigation
Rutherford | TELARAH 33 PA08 | N-1 | 2024 | 295 | 247 | 156 | 156 | 156 | Existing | Project under development
Rutherford | TELARAH 33 PA10 | N-1 | 2024 | 295 | 203 | 64 | 64 | 64 | Existing | Project under development
Chisholm | THORNTON 33 PA04 | N-1 | 2025 | 383 | 174 | 88 | 88 | 88 | Existing | Project in delivery
Thornton | THORNTON 33 PA11 | N-1 | 2024 | 310 | 223 | 145 | 145 | 190 | Existing | Project in delivery
Thornton | THORNTON 33 PA18 | N-1 | 2024 | 290 | 318 | 196 | 196 | 196 | Existing | Project under development
Chisholm | THORNTON 33 PA20 | N-1 | 2025 | 380 | 252 | 108 | 108 | 348 | Existing | Project in delivery
Tighes Hill / Islington | TIGHES HILL PA09 | N-1 | 2025 | 400 | 144 | 47 | 47 | 47 | 2026 | Project under development
Broadmeadow | TIGHES HILL PA17 | N-1 | 2025 | 400 | 216 | 38 | 38 | 38 | Existing | Project under development
Nelson Bay | TOMAREE 33 PA13 | N-1 | 2025 | 400 | 217 | 75 | 75 | 75 | Existing | Under investigation
Coal Point | TORONTO WEST 132 PA08 | N-1 | 2025 | 335 | 203 | 24 | 24 | 24 | Existing | Under investigation
Gosford | WEST GOSFORD PA03 | N-1 | 2025 | 365 | 168 | 0 | 82 | 163 | 2026 | Under investigation
Gosford | WEST GOSFORD PA12 | N-1 | 2025 | 400 | 305 | 28 | 28 | 28 | Existing | Under investigation
Williamtown | WILLIAMTOWN PA01 | N-1 | 2025 | 224 | 122 | 246 | 246 | 246 | Existing | Project in delivery
Fern Bay | WILLIAMTOWN PA02 | N-1 | 2025 | 148 | 13 | 103 | 103 | 103 | Existing | Under investigation
Williamtown | WILLIAMTOWN PA04 | N-1 | 2025 | 484 | 29 | 0 | 80 | 160 | 2026 | Project in delivery
Saratoga | WOY WOY PA06 | N-1 | 2025 | 290 | 58 | 32 | 32 | 32 | Existing | Under investigation
Warnervale | WYONG PA03 | N-1 | 2025 | 285 | 106 | 50 | 100 | 100 | Existing | Project under development
Jilliby | WYONG PA05 | N-1 | 2024 | 285 | 220 | 76.4993 | 76 | 76 | Existing | Project under development
Tacoma | WYONG PA10 | N-1 | 2024 | 355 | 238 | 216.415 | 216 | 216 | Existing | Project under development
Wyong Creek | WYONG PA12 | N-1 | 2024 | 370 | 120 | 74.248 | 74 | 74 | Existing | Project under development
Jilliby | WYONG PA14 | N-1 | 2025 | 400 | 183 | 217 | 217 | 217 | Existing | Project under development
Waterloo | ZETLAND PA10 | N-1 | 2025 | 355 | 186 | 26 | 26 | 26 | Existing | Project under development

## 2025 DTAPR FINAL OLD (hidden)
Location | Feeder Name | Type of risk | Year Identified | Rating (Amps) | 2024/25 Load (11kV amps) | 25/26 N-1 Load at Risk (11kV Amps) | 26/27 N-1 Load at Risk (11kV Amps) | 27/28 N-1 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution | Check Load | Comments
Speers Point | ARGENTON 132/11 PA11 | N-1 | 2024 | 400 | 322 | 179 | 179 | 179 | Existing | Under investigation
Macmasters Beach | AVOCA PA24 | N-1 | 2024 | 280 | 158 | 45 | 45 | 45 | Existing | Under investigation
Macmasters Beach | AVOCA PA33 | N-1 | 2024 | 325 | 156 | 21 | 21 | 21 | Existing | Under investigation
Punchbowl | BANKSTOWN PA10 | N-1 | 2025 | 300 | 174 | 50 | 50 | 50 | Existing | Under investigation
Brooklyn / Somersby | BEROWRA PA11 | N-1 | 2025 | 350 | 86 | 32 | 32 | 32 | Existing | Project in delivery
Cowan | BEROWRA PA21 | N-1 | 2025 | 350 | 189 | 104 | 104 | 104 | Existing | Under investigation
Blakehurst | BLAKEHURST PA1 | N-1 | 2025 | 355 | 186 | 156 | 156 | 156 | Existing | Under investigation
Blakehurst | BLAKEHURST PA12 | N-1 | 2025 | 355 | 179 | 90 | 90 | 90 | Existing | Under investigation
Branxton | BRANXTON 66 PA13 | N-1 | 2024 | 400 | 232 | 85 | 85 | 85 | Existing | Project under development
Burwood | BURWOOD PA09 | N-1 | 2025 | 390 | 266 | 53 | 53 | 53 | Existing | Under investigation
Canada Bay | BURWOOD PA19 | N-1 | 2025 | 400 | 158 | 136 | 136 | 136 | Existing | Under investigation
Cardiff | CARDIFF 33 PA01 | N-1 | 2025 | 301 | 236 | 46 | 46 | 46 | Existing | Under investigation
Warners Bay | CARDIFF 33 PA12 | N-1 | 2025 | 301 | 208 | 22 | 22 | 22 | Existing | Under investigation
Cardiff | CARDIFF 33 PA16 | N-1 | 2025 | 301 | 245 | 80 | 80 | 80 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA02 | N-1 | 2024 | 335 | 275 | 180 | 180 | 180 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA07 | N-1 | 2025 | 305 | 203 | 60 | 60 | 60 | Existing | Under investigation
Charlestown | CHARLESTOWN 132 PA08 | N-1 | 2025 | 400 | 384 | 119 | 119 | 119 | Existing | Under investigation
Woongarrah | CHARMHAVEN PA01 | N-1 | 2024 | 355 | 314 | 38 | 38 | 38 | Existing | Project in delivery | 1 | From ION
Hamlyn Terrace | CHARMHAVEN PA09 | N-1 | 2025 | 305 | 255 | 104 | 104 | 104 | Existing | Project under development | 1 | From ION
Woongarrah | CHARMHAVEN PA10 | N-1 | 2025 | 315 | 224 | 66 | 66 | 66 | Existing | Project under development | 1 | From ION
Woongarrah | CHARMHAVEN PA12 | N-1 | 2025 | 370 | 120 | 0 | 72 | 72 | 2026 | Project in delivery | 1 | From ION. Not confident in LAR, expected over estimated, scaled by 1/2, was 120
Lane Cove | CHATSWOOD PA37 | N-1 | 2025 | 320 | 164 | 194 | 194 | 194 | Existing | Project under development
Lane Cove | CHATSWOOD PA40 | N-1 | 2025 | 400 | 335 | 110 | 110 | 110 | Existing | Project under development
Breakfast Point | CONCORD PA04 | N-1 | 2024 | 320 | 203 | 119 | 119 | 119 | Existing | Project in delivery
Breakfast Point | CONCORD PA17 | N-1 | 2024 | 305 | 180 | 165 | 165 | 165 | Existing | Project in delivery
Breakfast Point | CONCORD PA18 | N-1 | 2024 | 315 | 185 | 79 | 79 | 79 | Existing | Project in delivery
Breakfast Point | CONCORD PA22 | N-1 | 2024 | 315 | 177 | 135 | 135 | 135 | Existing | Project in delivery
Warners Bay | CROUDANCE BAY PA01 | N-1 | 2025 | 282 | 284 | 196 | 196 | 196 | Existing | Under investigation
Valentine | CROUDANCE BAY PA02 | N-1 | 2025 | 373 | 114 | 69 | 69 | 69 | Existing | Under investigation
Belmont | CROUDANCE BAY PA06 | N-1 | 2025 | 373 | 260 | 104 | 104 | 104 | Existing | Under investigation
Valentine | CROUDANCE BAY PA12 | N-1 | 2025 | 337 | 279 | 206 | 206 | 206 | Existing | Under investigation
Pyrmont | DARLING HARBOUR 132/11kV PA09 | N-1 | 2025 | 400 | 287 | 40 | 40 | 40 | Existing | Project in delivery
Cameron Park | EDGEWORTH 33 PA01 | N-1 | 2024 | 293 | 293 | 51 | 51 | 51 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA07 | N-1 | 2025 | 258 | 216 | 41 | 41 | 41 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA09 | N-1 | 2024 | 263 | 197 | 100 | 100 | 100 | Existing | Under investigation
Holmesville | EDGEWORTH 33 PA10 | N-1 | 2024 | 400 | 359 | 108 | 108 | 108 | Existing | Under investigation
Kilcare | EMPIRE BAY PA08 | N-1 | 2024 | 400 | 176 | 87 | 87 | 87 | Existing | Under investigation
Green Point | ERINA PA01 | N-1 | 2025 | 400 | 195 | 33 | 33 | 33 | Existing | Under investigation
Erina | ERINA PA07 | N-1 | 2025 | 400 | 266 | 123 | 123 | 123 | Existing | Under investigation
Erina | ERINA PA13 | N-1 | 2025 | 280 | 173 | 35 | 35 | 35 | Existing | Under investigation | 1 | From ION
Homebush | FLEMINGTON PA04 | N-1 | 2025 | 300 | 185 | 175 | 175 | 175 | Existing | Project under development
Putney | HUNTERS HILL PA36 | N-1 | 2025 | 340 | 158 | 50 | 50 | 50 | Existing | Under investigation
Riverview | HUNTERS HILL PA41 | N-1 | 2025 | 330 | 155 | 47 | 47 | 47 | Existing | Under investigation
Riverview | HUNTERS HILL PA57 | N-1 | 2025 | 315 | 159 | 38 | 38 | 38 | Existing | Under investigation
Woronora | JANNALI PA25 | N-1 | 2025 | 315 | 121 | 75 | 75 | 75 | Existing | Under investigation | 1 | From ION. Not confident in LAR, expected over estimated, scaled by 1/2, was 150
Kurri Kurri | KURRI 132/11kV PA06 | N-1 | 2024 | 400 | 242 | 162 | 162 | 162 | Existing | Under investigation
Heddon Greta | KURRI 132/11kV PA12 | N-1 | 2025 | 400 | 306 | 50 | 50 | 50 | Existing | Under investigation
Gillieston Heights | KURRI 132/11kV PA19 | N-1 | 2024 | 400 | 329 | 115 | 115 | 115 | Existing | Under investigation
Summerland Point | LAKE MUNMORAH PA07 | N-1 | 2024 | 390 | 382 | 152.3997 | 152 | 152 | Existing | Under investigation
Bateau Bay | LONG JETTY PA02 | N-1 | 2024 | 280 | 176 | 145 | 145 | 145 | Existing | Under investigation
Maitland Vale | MAITLAND 33 PA04 | N & N-1 | 2024 | 270 | 291 | 240 | 240 | 240 | Existing | Project under development | 1 | From ION
Aberglasslyn | MAITLAND 33 PA07 | N & N-1 | 2024 | 290 | 310 | 249 | 249 | 249 | Existing | Project under development
Largs | MAITLAND 33 PA11 | N & N-1 | 2024 | 260 | 257 | 133 | 133 | 133 | Existing | Project under development
Bolwarra Heights | MAITLAND 33 PA13 | N-1 | 2024 | 260 | 226 | 193 | 193 | 193 | Existing | Project under development
Fletcher | MARYLAND 132 PA02 | N-1 | 2024 | 384 | 238 | 67 | 67 | 67 | Existing | Under investigation
Fletcher | MARYLAND 132 PA06 | N-1 | 2024 | 384 | 290 | 53 | 53 | 53 | Existing | Under investigation
Cameron Park | MARYLAND 132 PA10 | N-1 | 2024 | 400 | 102 | 26 | 26 | 26 | Existing | Under investigation
Muswellbrook | MITCHELL LINE 66 PA11 | N-1 | 2024 | 400 | 199 | 100 | 100 | 100 | Existing | Project under development
Wyee | MORISSET 132 PA06 | N-1 | 2024 | 364 | 251 | 64 | 64 | 64 | Existing | Project under development
Mosman | MOSMAN PA36 | N-1 | 2025 | 350 | 112 | 26 | 26 | 26 | Existing | Under investigation
Eleebana | MT HUTTON PA03 | N-1 | 2025 | 288 | 255 | 53 | 53 | 53 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA03 | N-1 | 2025 | 398 | 163 | 31 | 31 | 31 | Existing | Under investigation
Soldiers Point | NELSON BAY 33 PA04 | N-1 | 2024 | 282 | 232 | 109 | 109 | 109 | Existing | Under investigation
Nelson Bay | NELSON BAY 33 PA05 | N-1 | 2025 | 263 | 211 | 124 | 124 | 124 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA09 | N-1 | 2025 | 385 | 147 | 183 | 183 | 183 | Existing | Under investigation
Bar Beach | NEWCASTLE CBD 33 PA30 | N-1 | 2024 | 265 | 241 | 26 | 26 | 26 | Existing | Under investigation
Cessnock | NULKABA 33 PA05 | N-1 | 2025 | 400 | 277 | 93 | 93 | 93 | Existing | Under investigation
Homebush | OLYMPIC PARK PA06 | N-1 | 2025 | 400 | 184 | 88 | 88 | 88 | Existing | Project under development
Homebush | OLYMPIC PARK PA10 | N-1 | 2025 | 400 | 108 | 121 | 121 | 121 | Existing | Project under development
Blacksmiths | PELICAN 33 PA01 | N-1 | 2025 | 400 | 178 | 46 | 46 | 46 | Existing | Under investigation
Rathmines | RATHMINES 132 PA10 | N-1 | 2024 | 288 | 197 | 180 | 180 | 180 | Existing | Under investigation
Raymond Terrace | RAYMOND TERRACE 33 PA04 | N-1 | 2025 | 308 | 51 | 20 | 20 | 20 | Existing | Under investigation
Rose Bay | ROSE BAY PA13 | N-1 | 2025 | 290 | 195 | 78 | 78 | 78 | Existing | Under investigation
Aberglasslyn | RUTHERFORD 33 PA02 | N & N-1 | 2024 | 350 | 447 | 396 | 396 | 396 | Existing | Project under development | 1 | From ION
Rutherford | RUTHERFORD 33 PA03 | N-1 | 2024 | 380 | 281 | 36 | 36 | 36 | Existing | Project under development
Rutherford | RUTHERFORD 33 PA09 | N-1 | 2024 | 350 | 161 | 151 | 151 | 151 | Existing | Project under development
Whittingham / Abattoir | SINGLETON 66 PA28 | N-1 | 2024 | 400 | 244 | 145 | 145 | 145 | Existing | Under investigation
Kariong | SOMERSBY PA16 | N-1 | 2025 | 295 | 219 | 32 | 32 | 32 | Existing | Under investigation
Somersby | SOMERSBY PA17 | N-1 | 2024 | 295 | 85 | 63 | 63 | 63 | Existing | Under investigation
Redfern | ST. PETERS PA20 | N-1 | 2025 | 400 | 212 | 28 | 28 | 28 | Existing | Under investigation
Erskineville | ST. PETERS PA32 | N-1 | 2025 | 316 | 197 | 45 | 45 | 45 | Existing | Under investigation
Tanilba Bay | TANILBA BAY 33 PA15 | N-1 | 2025 | 337 | 176 | 100 | 100 | 100 | Existing | Under investigation | 1 | From ION. Not confident in LAR, expected over estimated, scaled by 1/2, was 200
Rutherford | TELARAH 33 PA08 | N-1 | 2024 | 295 | 247 | 156 | 156 | 156 | Existing | Project under development
Rutherford | TELARAH 33 PA10 | N-1 | 2024 | 295 | 203 | 64 | 64 | 64 | Existing | Project under development
Chisholm | THORNTON 33 PA04 | N-1 | 2025 | 383 | 174 | 88 | 88 | 88 | Existing | Project in delivery
Thornton | THORNTON 33 PA11 | N-1 | 2024 | 310 | 223 | 145 | 145 | 190 | Existing | Project in delivery
Thornton | THORNTON 33 PA18 | N-1 | 2024 | 290 | 318 | 196 | 196 | 196 | Existing | Project under development
Chisholm | THORNTON 33 PA20 | N-1 | 2025 | 380 | 252 | 108 | 108 | 348 | Existing | Project in delivery
Tighes Hill / Islington | TIGHES HILL PA09 | N-1 | 2025 | 400 | 144 | 47 | 47 | 47 | 2026 | Project under development
Broadmeadow | TIGHES HILL PA17 | N-1 | 2025 | 400 | 216 | 38 | 38 | 38 | Existing | Project under development |  | 163.2
Nelson Bay | TOMAREE 33 PA13 | N-1 | 2025 | 400 | 217 | 75 | 75 | 75 | Existing | Under investigation
Coal Point | TORONTO WEST 132 PA08 | N-1 | 2025 | 335 | 203 | 24 | 24 | 24 | Existing | Under investigation
Gosford | WEST GOSFORD PA03 | N-1 | 2025 | 365 | 168 | 0 | 82 | 163 | 2026 | Under investigation | 1 | From ION. Not confident in LAR, expected over estimated, scaled by 1/2, was 272
Gosford | WEST GOSFORD PA12 | N-1 | 2025 | 400 | 305 | 28 | 28 | 28 | Existing | Under investigation
Williamtown | WILLIAMTOWN PA01 | N-1 | 2025 | 224 | 122 | 246 | 246 | 246 | Existing | Project in delivery
Fern Bay | WILLIAMTOWN PA02 | N-1 | 2025 | 148 | 13 | 103 | 103 | 103 | Existing | Under investigation
Williamtown | WILLIAMTOWN PA04 | N-1 | 2025 | 484 | 29 | 0 | 80 | 160 | 2026 | Project in delivery | 1 | Forecast LAR, Newcastle Airport Precint. Not confident in LAR, reduced by 1/2 and forecast year made 2026
Saratoga | WOY WOY PA06 | N-1 | 2025 | 290 | 58 | 32 | 32 | 32 | Existing | Under investigation
Warnervale | WYONG PA03 | N-1 | 2025 | 285 | 106 | 50 | 100 | 100 | Existing | Project under development | 1 | From ION. Not confident in LAR, expected over estimated, scaled by 1/2, was 167
Jilliby | WYONG PA05 | N-1 | 2024 | 285 | 220 | 76.4993 | 76 | 76 | Existing | Project under development
Tacoma | WYONG PA10 | N-1 | 2024 | 355 | 238 | 216.415 | 216 | 216 | Existing | Project under development
Wyong Creek | WYONG PA12 | N-1 | 2024 | 370 | 120 | 74.248 | 74 | 74 | Existing | Project under development | 1 | From ION
Jilliby | WYONG PA14 | N-1 | 2025 | 400 | 183 | 217 | 217 | 217 | Existing | Project under development
Waterloo | ZETLAND PA10 | N-1 | 2025 | 355 | 186 | 26 | 26 | 26 | Existing | Project under development
100.2
[7 empty] | 268 | 160.8

## 2025 RAW (hidden)
Zone | Panel | Panel OMS | Zone | Area Plan | Total LAR | LAR Events per fdr | Ave LAR Per Event | Max LAR All | Max LAR (Capped at 150) | Location (Main suburb) | Feeder Name (MJ) | Type of risk | Year Identified | Feeder Trunk Rating (Amps) (MJ from SON) | 2024/25 Load (11kV amps (MJ SON)) | 24/25 Load at Risk (11kV Amps) | 25/26 Load at Risk (11kV Amps) | 26/27 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution | Comments | Please update green
ZN00256 | CBZZN00256PA23 | 256:80647 | ADAMSTOWN 132 | Newcastle Inner City | 57 | 1 | 57 | 57 | 57 | Hamilton |  | N-1 | 2025 |  |  | 57 | 57 | 57 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025 |  | Check LAR
ZN00224 | CBZZN00224PA11 | 224:80346 | ARGENTON 132/11 | Newcastle Western Corridor | 178.6974 | 1 | 178.6974 | 178.6974 | 150 | Speers Point |  | N-1 | 2024 |  |  | 179 | 179 | 179 | Existing | Under investigation |  |  | Project in delivery
ZN12570 | CBZZN12570PA22 | ZN12570:PA22 | AVOCA | Lower Central Coast | 207.8234 | 4 | 51.9558 | 81.922 | 81.922 | Saratoga |  | N-1 | 2025 |  |  | 12 | 12 | 12 | 2025 | Under investigation | LAR identified as much lower in recent LAR results Nov 2025 |  | Project under development
ZN12570 | CBZZN12570PA24 | ZN12570:PA24 | AVOCA | Lower Central Coast | 328.5584 | 5 | 65.7117 | 164 | 150 | MacMasters Beach |  | N-1 | 2024 |  |  | 45 | 45 | 45 | 2024 | Under investigation | LAR identified as much lower in recent LAR results Nov 2025 |  | Under investigation
ZN12570 | CBZZN12570PA26 | ZN12570:PA26 | AVOCA | Lower Central Coast | 71 | 2 | 35.5 | 42 | 42 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12570 | CBZZN12570PA40 | ZN12570:PA40 | AVOCA | Lower Central Coast | 175.2209 | 2 | 87.6104 | 105.2401 | 105.2401 | Davistown |  | N-1 | 2024 |  |  | 12 | 12 | 12 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12570 | CBZZN12570PA33 | ZN12570:PA33 | AVOCA | Lower Central Coast | 187.9545 | 4 | 46.9886 | 60.6129 | 60.6129 | MacMasters Beach |  | N-1 | 2024 |  |  | 21 | 21 | 21 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12570 | CBZZN12570PA39 | ZN12570:PA39 | AVOCA | Lower Central Coast | 13 | 1 | 13 | 13 | 0 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12570 | CBZZN12570PA37 | ZN12570:PA37 | AVOCA | Lower Central Coast | 100.6446 | 2 | 50.3223 | 67.2493 | 67.2493 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN35800 | CBZZN35800PA14 | ZN35800:PA14 | BANKSTOWN | Canterbury Bankstown | 669 | 3 | 223 | 342 | 150 | Bankstown |  | N-1 | 2024 |  |  | 150 | 150 | 150 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN35800 | CBZZN35800PA10 | ZN35800:PA10 | BANKSTOWN | Canterbury Bankstown | 80.6593 | 3 | 26.8864 | 50 | 50 | Punchbowl |  | N-1 | 2025 |  |  | 50 | 50 | 50 | Existing | Under investigation
ZN01850 | CBZZN01850PA40 | ZN1850:PA40 | BASS HILL | Canterbury Bankstown | 52 | 1 | 52 | 52 | 52 | Georges Hall |  | N-1 | 2025 |  |  | 52 | 52 | 52 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12690 | CBZZN12690PA26 | ZN12690:PA26 | BERKELEY VALE | Lower Central Coast |  |  |  | 70 | 70 | Tuggerah |  | N-1 | 2025 |  |  | 70 | 70 | 70 | 2025 | Check LAR | LAR identified in recent LAR Resullts in Nov 2025
ZN12690 | CBZZN12690PA17 | ZN12690:PA17 | BERKELEY VALE | Lower Central Coast |  |  |  | 63 | 63 | Tuggerah |  | N-1 | 2025 |  |  | 63 | 63 | 63 | 2025 | Check LAR | LAR identified in recent LAR Resullts in Nov 2025
ZN12690 | CBZZN12690PA07 | ZN12690:PA7 | BERKELEY VALE | Lower Central Coast | 54 | 2 | 27 | 34 | 34 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN02400 | CBZZN02400PA11 | ZN2400:PA11 | BEROWRA | North West Sydney | 62 | 2 | 31 | 32 | 32 | Brooklyn / Somersby |  | N-1 | 2025 |  |  | 32 | 32 | 32 | 2025 | Project in delivery | Project initiated to loop in FDR with Somersby Zn PA17.
ZN02400 | CBZZN02400PA15 | ZN2400:PA15 | BEROWRA | North West Sydney | 109 | 1 | 109 | 109 | 109 | Mt. Kuringai |  | N-1 | 2025 |  |  | 109 | 109 | 109 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN02400 | CBZZN02400PA18 | ZN2400:PA18 | BEROWRA | North West Sydney | 110.5382 | 2 | 55.2691 | 61 | 61 | Berowra Waters |  | N-1 | 2025 |  |  | 61 | 61 | 61 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN02400 | CBZZN02400PA21 | ZN2400:PA21 | BEROWRA | North West Sydney | 161.0804 | 2 | 80.5402 | 104 | 104 | Cowan |  | N-1 | 2025 |  |  | 104 | 104 | 104 | 2025 | Under investigation | Assoc. with the above project (PA11). When Proj. completed, being able to move approx. 97A (PA11, CP2715) to Somersby PA17 will fix this problem.
ZN02400 | CBZZN02400PA26 | ZN2400:PA26 | BEROWRA | North West Sydney | 128 | 2 | 64 | 83 | 83 | Berowra Heights |  | N-1 | 2025 |  |  | 83 | 83 | 83 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN10991 | CBZZN10991PA01 | ZN10991:PA1 | BLAKEHURST | St George | 102.7146 | 2 | 51.3573 | 90.7146 | 90.7146 | Blakehurst |  | N-1 | 2025 |  |  | 156 | 156 | 156 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR unverified
ZN10991 | CBZZN10991PA08 | ZN10991:PA8 | BLAKEHURST | St George | 48.4897 | 2 | 24.2448 | 29.4897 | 29.4897 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN10991 | CBZZN10991PA12 | ZN10991:PA12 | BLAKEHURST | St George | 166 | 3 | 55.3333 | 69 | 69 | Blakehurst |  | N-1 | 2025 |  |  | 90 | 90 | 90 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR unverified
ZN00340 | CBZZN00340PA44 | ZN340:PA44 | BOTANY | Eastern Suburbs | 38 | 1 | 38 | 38 | 38 | Pagewood |  | N-1 | 2025 |  |  | 38 | 38 | 38 | 2025 | Check LAR | Does not show up on the most recent LAR tool
ZN00508 | CBZZN00508PA13 | 508:82579 | BRANDY HILL 132 | Maitland | 107.6 | 2 | 53.8 | 54.441 | 54.441 | Wallalong |  | N-1 | 2025 |  |  | 19 | 19 | 19 | Existing | Under investigation
ZN00512 | CBZZN00512PA13 | 512:83736 | BRANXTON 66 | Singleton | 149.0566 | 2 | 74.5283 | 85.0566 | 85.0566 | Branxton |  | N-1 | 2024 |  |  | 85 | 85 | 85 | Existing | Project under development | Flagged by recent LAR tool run on Dev models, LAR verified, awaiting options analysis
ZN00257 | CBZZN00257PA09 | 257:81994 | BROADMEADOW 132 | Newcastle Inner City | 47 | 1 | 47 | 47 | 47 | Waratah |  | N-1 | 2025 |  |  | 47 | 47 | 47 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025
ZN00257 | CBZZN00257PA24 | 257:81987 | BROADMEADOW 132 | Newcastle Inner City | 210 | 3 | 70 | 132 | 132 | Waratah |  | N-1 | 2025 |  |  | 132 | 132 | 132 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025
ZN15001 | CBZZN15001PA10 | ZN15001:PA10 | BROOKVALE | Manly Warringah | 25 | 1 | 25 | 25 | 25 | Brookvale |  | N-1 | 2025 |  |  | 25 | 25 | 25 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN02835 |  | PA9 | BURWOOD | Inner West Sydney | [5 empty] | Burwood |  | N-1 | 2025 |  |  | 53 | 53 | 53 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR verified, awaiting options analysis
ZN02835 |  | PA15 | BURWOOD | Inner West Sydney | [5 empty] | Homebush |  | N-1 | 2025 |  |  | 18 | 18 | 18 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN02835 |  | PA19 | BURWOOD | Inner West Sydney | [5 empty] | Canada Bay |  | N-1 | 2025 |  |  | 136 | 136 | 136 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR verified, awaiting options analysis
ZN02835 |  | PA30 | BURWOOD | Inner West Sydney | [5 empty] | Concord |  | N-1 | 2025 |  |  | 17 | 17 | 17 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR verified, awaiting options analysis
ZN02835 |  | PA33 | BURWOOD | Inner West Sydney | [5 empty] | Homebush |  | N-1 | 2025 |  |  | 10 | 10 | 10 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN00690 | CBZZN00690PA04 | ZN690:PA4 | CAMPSIE | Canterbury Bankstown | 23 | 1 | 23 | 23 | 23 | Canturbury |  | N-1 | 2025 |  |  | 23 | 23 | 23 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00690 | CBZZN00690PA34 | ZN690:PA34 | CAMPSIE | Canterbury Bankstown | 109 | 2 | 54.5 | 57 | 57 | Campsie |  | N-1 | 2025 |  |  | 57 | 57 | 57 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00690 | CBZZN00690PA28 | ZN690:PA28 | CAMPSIE | Canterbury Bankstown | 22.8234 | 1 | 22.8234 | 22.8234 | 22.8234 | Campsie |  | N-1 | 2024 |  |  | 23 | 23 | 23 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00690 | CBZZN00690PA18 | ZN690:PA18 | CAMPSIE | Canterbury Bankstown | 76 | 1 | 76 | 76 | 76 | Belmore |  | N-1 | 2025 |  |  | 76 | 76 | 76 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00690 | CBZZN00690PA35 | ZN690:PA35 | CAMPSIE | Canterbury Bankstown | 129 | 3 | 43 | 58 | 58 | Campsie |  | N-1 | 2025 |  |  | 58 | 58 | 58 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00690 | CBZZN00690PA36 | ZN690:PA36 | CAMPSIE | Canterbury Bankstown | 29.4672 | 1 | 29.4672 | 29.4672 | 29.4672 | Earlwood |  | N-1 | 2024 |  |  | 29 | 29 | 29 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00214 | CBZZN00214PA01 | 214:8666 | CARDIFF 33 | Newcastle Western Corridor | 46 | 1 | 46 | 46 | 46 | Cardiff |  | N-1 | 2025 |  |  | 46 | 46 | 46 | Existing | Under investigation
ZN00214 | CBZZN00214PA12 | 214:8670 | CARDIFF 33 | Newcastle Western Corridor | 22 | 1 | 22 | 22 | 22 | Warners Bay |  | N-1 | 2025 |  |  | 22 | 22 | 22 | Existing | Under investigation
ZN00214 | CBZZN00214PA16 | 214:8665 | CARDIFF 33 | Newcastle Western Corridor | 80 | 1 | 80 | 80 | 80 | Cardiff |  | N-1 | 2025 |  |  | 80 | 80 | 80 | Existing | Under investigation
ZN15010 | CBZZN15010PA30 | ZN15010:PA30 | CAREEL BAY | Pittwater & Northern Beaches | 46 | 1 | 46 | 46 | 46 | Avalon |  | N-1 | 2025 |  |  | 46 | 46 | 46 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN00522 | CBZZN00522PA02 | 522:83123 | CESSNOCK SOUTH | Greater Cessnock | 387.5055 | 3 | 129.1685 | 179.6087 | 150 | Cessnock |  | N-1 | 2024 |  |  | 180 | 180 | 180 | Existing | Under investigation
ZN00522 | CBZZN00522PA07 | 522:83129 | CESSNOCK SOUTH | Greater Cessnock | 60 | 1 | 60 | 60 | 60 | Cessnock |  | N-1 | 2025 |  |  | 60 | 60 | 60 | Existing | Under investigation
ZN00522 | CBZZN00522PA11 | 522:83132 | CESSNOCK SOUTH | Greater Cessnock | 10.6867 | 1 | 10.6867 | 10.6867 | 0 | Kitchener |  | N-1 | 2024 |  |  | 11 | 11 | 11 | Existing | Under investigation
ZN00261 | CBZZN00261PA08 | 261:81879 | CHARLESTOWN 132 | North East Lake Macquarie | 293 | 3 | 97.6667 | 119 | 119 | CHARLESTOWN |  | N-1 | 2025 |  |  | 119 | 119 | 119 | 2025 | Under investigation | No LAR identified in "LAR Resullts 20251106", suspect issues trunks loaded 93%
ZN00261 | CBZZN00261PA23 | 261:81870 | CHARLESTOWN 132 | North East Lake Macquarie | 39 | 1 | 39 | 39 | 39 | GARDEN SUBURB |  | N-1 | 2025 |  |  | 39 | 39 | 39 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN00261 | CBZZN00261PA15 | 261:81882 | CHARLESTOWN 132 | North East Lake Macquarie | 85 | 1 | 85 | 85 | 85 | CHARLESTOWN |  | N-1 | 2025 |  |  | 85 | 85 | 85 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14892 | CBZZN14892PA01 | ZN14892:PA1 | CHARMHAVEN | Upper Central Coast | 38 | 1 | 38 | 38 | 38 | WOONGARRAH |  | N-1 | 2024 |  |  | 38 | 38 | 38 | 2024 | Project in delivery | LAR was identified in "LAR Resullts 20251106" project issued new PA20R $1,566,000
ZN14892 | CBZZN14892PA06 | ZN14892:PA6 | CHARMHAVEN | Upper Central Coast | 37.9967 | 1 | 37.9967 | 37.9967 | 37.9967 | BLUE HAVEN |  | N-1 | 2025 |  |  | 37.9967 | 38 | 38 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14892 | CBZZN14892PA16 | ZN14892:PA16 | CHARMHAVEN | Upper Central Coast | 227 | 3 | 75.6667 | 91 | 91 | SAN REMO |  | N-1 | 2025 |  |  | 91 | 91 | 91 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14892 | CBZZN14892PA19 | ZN14892:PA19 | CHARMHAVEN | Upper Central Coast | 44 | 1 | 44 | 44 | 44 | GOROKAN |  | N-1 | 2025 |  |  | 44 | 44 | 44 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14892 | CBZZN14892PA13 | ZN14892:PA13 | CHARMHAVEN | Upper Central Coast | 73 | 1 | 73 | 73 | 73 | KANWAL |  | N-1 | 2025 |  |  | 73 | 73 | 73 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14892 | CBZZN14892PA13 | ZN14892:PA09 | CHARMHAVEN | Upper Central Coast | [5 empty] | HAMLYN TERRACE |  | N-1 | 2025 |  |  | 104 |  |  | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN14892 | CBZZN14892PA13 | ZN14892:PA10 | CHARMHAVEN | Upper Central Coast | [5 empty] | WOONGARRAH |  | N-1 | 2025 |  |  | 66 |  |  | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN14892 | CBZZN14892PA13 | ZN14892:PA12 | CHARMHAVEN | Upper Central Coast | [5 empty] | WOONGARRAH |  | N-1 | 2025 |  |  | 120 |  |  | 2025 | Project in delivery | LAR was identified in "LAR Resullts 20251106" project issued new PA20R $1,566,000 | NEW ROW ADDED
ZN00080 | CBZZN00080PA37 | ZN80:PA37 | CHATSWOOD | Lower North Shore | [7 empty] | N-1 | 2025 |  |  | 194 | 194 | 194 | 2025 | Project under development | Latest N-1 results identified this feeder as an N-1 LAR issue as of 7 Nov 2025. PI-2025_1193 is investigating possible solutions.
ZN00080 | CBZZN00080PA40 | ZN80:PA40 | CHATSWOOD | Lower North Shore | [7 empty] | N-1 | 2025 |  |  | 110 | 110 | 110 | 2025 | Project under development | Latest N-1 results identified this feeder as an N-1 LAR issue as of 7 Nov 2025. PI-2025_1193 is investigating possible solutions.
ZN02602 | CBZZN02602PA42 | ZN2602:PA42 | CLOVELLY | Eastern Suburbs | 11 | 1 | 11 | 11 | 0 | Kengsington |  | N-1 | 2025 |  |  | 65 | 65 | 65 | 2025 | Check LAR | Does not show up on the most recent LAR tool
ZN00874 | CBZZN00874PA04 | ZN874:PA4 | CONCORD | Inner West Sydney | 65 | 1 | 65 | 65 | 65 | Breakfast Point |  | N-1 | 2021 |  |  | 119 | 119 | 119 | 2021 | Project in delivery | PI-2021_1339
ZN00874 |  | PA17 | CONCORD | Inner West Sydney | [5 empty] | Breakfast Point |  | N-1 | 2021 |  |  | 165 | 165 | 165 | 2021 | Project in delivery | PI-2021_1339
ZN00874 |  | PA18 | CONCORD | Inner West Sydney | 65 | 1 | 65 |  |  | Breakfast Point |  | N-1 | 2021 |  |  | 79 | 79 | 79 | 2021 | Project in delivery | PI-2021_1339
ZN00874 |  | PA22 | CONCORD | Inner West Sydney | 65 | 1 | 65 |  |  | Breakfast Point |  | N-1 | 2021 |  |  | 135 | 135 | 135 | 2021 | Project in delivery | PI-2021_1339
ZN00206 | CBZZN00206PA01 | 206:34441 | CROUDANCE BAY | North East Lake Macquarie | [5 empty] | WARNERS BAY |  | N-1 | 2025 |  |  | 196 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00206 | CBZZN00206PA02 | 206:34438 | CROUDANCE BAY | North East Lake Macquarie | [5 empty] | VALENTINE |  | N-1 | 2025 |  |  | 69 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00206 | CBZZN00206PA06 | 206:34432 | CROUDANCE BAY | North East Lake Macquarie | [5 empty] | BELMONT |  | N-1 | 2025 |  |  | 104 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00206 | CBZZN00206PA12 | 206:34434 | CROUDANCE BAY | North East Lake Macquarie | [5 empty] | VALENTINE |  | N-1 | 2025 |  |  | 206 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00187 | CBZZN00187PA17 | ZN187:PA17 | CROWS NEST | Lower North Shore | 32.1019 | 1 | 32.1019 | 32.1019 | 32.1019 | Cammeray | [6 empty] | 0 | 0 |  | Check LAR | Latest N-1 results show no LAR as of Nov 2025
ZN00187 | CBZZN00187PA30 | ZN187:PA30 | CROWS NEST | Lower North Shore | 19 | 1 | 19 | 19 | 19 | Naremburn | [6 empty] | 0 | 0 |  | Check LAR | Latest N-1 results show no LAR as of Nov 2025
ZN07481 | CBZZN07481PA03 | ZN7481:PA3 | DARLING HARBOUR 132/11kV | Camperdown & Blackwattle Bay | 350.3821 | 1 | 350.3821 | 350.3821 | 150 | Pyrmont |  | N-1 | 2025 |  |  | 0 | 0 | 0 |  | Check LAR | LAR has been identified in LAR Tool Nov results but it was mitigated by amending a HVCon connection. No LAR.
ZN07481 | CBZZN07481PA09 | ZN7481:PA9 | DARLING HARBOUR 132/11kV | Camperdown & Blackwattle Bay | 299.3672 | 1 | 299.3672 | 299.3672 | 150 | Pyrmont |  | N-1 | 2025 |  |  | 40 | 40 | 40 | 2025 | Project in delivery | LAR. Project has been issued under PI2025_1138.
ZN15006 | CBZZN15006PA09 | ZN15006:PA9 | DEE WHY WEST | Manly Warringah | 8 | 1 | 8 | 8 | 0 | Dee Why |  | N-1 | 2025 |  |  | 8 | 8 | 8 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN00216 | CBZZN00216PA09 | 216:10729 | EDGEWORTH 33 | Newcastle Western Corridor | 99.6071 | 1 | 99.6071 | 99.6071 | 99.6071 | Cameron Park |  | N-1 | 2024 |  |  | 100 | 100 | 100 | Existing | Under investigation
ZN00216 | CBZZN00216PA10 | 216:10722 | EDGEWORTH 33 | Newcastle Western Corridor | 108.4778 | 1 | 108.4778 | 108.4778 | 108.4778 | Holmesville |  | N-1 | 2024 |  |  | 108 | 108 | 108 | Existing | Under investigation
ZN00216 | CBZZN00216PA01 | 216:10724 | EDGEWORTH 33 | Newcastle Western Corridor | 50.508 | 1 | 50.508 | 50.508 | 50.508 | Cameron Park |  | N-1 | 2024 |  |  | 51 | 51 | 51 | Existing | Under investigation
ZN00216 | CBZZN00216PA07 | 216:10728 | EDGEWORTH 33 | Newcastle Western Corridor | 41 | 1 | 41 | 41 | 41 | Cameron Park |  | N-1 | 2025 |  |  | 41 | 41 | 41 | Existing | Under investigation
ZN36200 | CBZZN36200PA01 | ZN36200:PA1 | EMPIRE BAY | Lower Central Coast | 114 | 3 | 38 | 69 | 69 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN36200 | CBZZN36200PA04 | ZN36200:PA4 | EMPIRE BAY | Lower Central Coast | 20.9769 | 1 | 20.9769 | 20.9769 | 20.9769 | Empire Bay |  | N-1 | 2024 |  |  | 11 | 11 | 11 |  | Under investigation | LAR identified in recent LAR results Nov 2025
ZN36200 | CBZZN36200PA08 | ZN36200:PA8 | EMPIRE BAY | Lower Central Coast | 31.7519 | 1 | 31.7519 | 31.7519 | 31.7519 | Kilcare |  | N-1 | 2024 |  |  | 87 | 87 | 87 |  | Under investigation | LAR identified in recent LAR results Nov 2025
ZN09245 | CBZZN09245PA19 | ZN9245:PA19 | ENGADINE | Sutherland | 12 | 1 | 12 | 12 | 0 | Engadine |  | N-1 | 2025 |  |  | 12 | 12 | 12 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12580 | CBZZN12580PA04 | ZN12580:PA4 | ERINA | Lower Central Coast | 64 | 2 | 32 | 54 | 54 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12580 | CBZZN12580PA13 | ZN12580:PA13 | ERINA | Lower Central Coast |  |  |  | 35 | 35 | Erina |  | N-1 | 2025 |  |  | 35 | 35 | 35 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12580 | CBZZN12580PA07 | ZN12580:PA7 | ERINA | Lower Central Coast |  |  |  | 123 | 123 | Erina |  | N-1 | 2025 |  |  | 123 | 123 | 123 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12580 | CBZZN12580PA01 | ZN12580:PA1 | ERINA | Lower Central Coast | 8 | 1 | 8 | 8 | 0 | Green Point |  | N-1 | 2025 |  |  | 33 | 33 | 33 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN02466 |  | PA4 | FLEMINGTON | Inner West Sydney | [5 empty] | Homebush |  | N-1 | 2025 |  |  | 175 | 175 | 175 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN02466 |  | PA6 | FLEMINGTON | Inner West Sydney | [5 empty] | Lidcombe |  | N-1 | 2025 |  |  | 10 | 10 | 10 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR verified, awaiting options analysis
ZN00129 | CBZZN00129PA36 | ZN129:PA36 | HUNTERS HILL | Carlingford | [5 empty] | Putney |  | N-1 | 2025 |  |  | 50 | 50 | 50 | 2025 | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN00129 | CBZZN00129PA41 | ZN129:PA41 | HUNTERS HILL | Carlingford | 37.9192 | 1 | 37.9192 | 37.9192 | 37.9192 | Riverview |  | N-1 | 2025 |  |  | 47 | 47 | 47 | Existing | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN00129 | CBZZN00129PA57 | ZN129:PA57 | HUNTERS HILL | Carlingford | [5 empty] | Riverview |  | N-1 | 2025 |  |  | 38 | 38 | 38 | 2025 | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN09252 | CBZZN09252PA27 | ZN9252:PA27 | JANNALI | Sutherland | 9 | 1 | 9 | 9 | 0 | Kareela |  | N-1 | 2025 |  |  | 9 | 9 | 9 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN09252 | CBZZN09252PA25 | ZN9252:PA25 | JANNALI | Sutherland | 152 | 1 | 152 | 152 | 150 | Woronora |  | N-1 | 2025 |  |  | 150 | 150 | 150 | Existing | Under investigation
ZN00258 | CBZZN00258PA12 | 258:80787 | JESMOND 132 | Newcastle Ports | 9 | 1 | 9 | 9 | 0 | Shortland |  | N-1 | 2025 |  |  | 9 | 9 | 9 | Existing | Under investigation
ZN35600 | CBZZN35600PA16 | ZN35600:PA16 | KINGSFORD | Eastern Suburbs | 59.7462 | 1 | 59.7462 | 59.7462 | 59.7462 | Kingsford |  | N-1 | 2025 |  |  | 60 | 60 | 60 | 2025 | Check LAR | Does not show up on the most recent LAR tool
ZN35600 | CBZZN35600PA19 | ZN35600:PA19 | KINGSFORD | Eastern Suburbs | 14 | 1 | 14 | 14 | 0 | Coogee |  | N-1 | 2025 |  |  |  | 0 | 0 | 2025 | Check LAR | Does not show up on the most recent LAR tool
ZN09700 | CBZZN09700PA15 | ZN9700:PA15 | KIRRAWEE | Sutherland | 59 | 1 | 59 | 59 | 59 | Grays Point |  | N-1 | 2025 |  |  | 59 | 59 | 59 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00205 | CBZZN00205PA03 | 205:12213 | KOTARA 33 | Newcastle Inner City | 23.5984 | 1 | 23.5984 | 23.5984 | 23.5984 | Kotara |  | N-1 | 2024 |  |  | 24 | 24 | 24 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025
ZN00507 | CBZZN00507PA06 | 507:80932 | KURRI 132/11kV | Greater Cessnock | 589.0087 | 6 | 98.1681 | 162 | 150 | Kurri Kurri |  | N-1 | 2024 |  |  | 162 | 162 | 162 | Existing | Under investigation
ZN00507 | CBZZN00507PA12 | 507:80914 | KURRI 132/11kV | Greater Cessnock | 50 | 1 | 50 | 50 | 50 | Heddon Greta |  | N-1 | 2025 |  |  | 50 | 50 | 50 | Existing | Under investigation
ZN00507 | CBZZN00507PA19 | 507:80923 | KURRI 132/11kV | Greater Cessnock | 114.5858 | 1 | 114.5858 | 114.5858 | 114.5858 | Gillieston Heights |  | N-1 | 2024 |  |  | 115 | 115 | 115 | Existing | Under investigation
ZN13000 | CBZZN13000PA10 | ZN13000:PA10 | LAKE MUNMORAH | Upper Central Coast | 25.6981 | 1 | 25.6981 | 25.6981 | 25.6981 | LAKE MUNMORAH |  | N-1 | 2024 |  |  | 25.6981 | 26 | 26 | 2024 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN13000 | CBZZN13000PA11 | ZN13000:PA11 | LAKE MUNMORAH | Upper Central Coast | 177.8743 | 3 | 59.2914 | 66.8315 | 66.8315 | MANNERING PARK |  | N-1 | 2024 |  |  | 66.8315 | 67 | 67 | 2024 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN13000 | CBZZN13000PA05 | ZN13000:PA5 | LAKE MUNMORAH | Upper Central Coast | 4 | 1 | 4 | 4 | 0 | DOYALSON |  | N-1 | 2025 |  |  | 4 | 4 | 4 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN13000 | CBZZN13000PA07 | ZN13000:PA7 | LAKE MUNMORAH | Upper Central Coast | 152.3997 | 1 | 152.3997 | 152.3997 | 150 | SUMMERLAND POINT |  | N-1 | 2024 |  |  | 152.3997 | 152 | 152 | 2024 | Under investigation | Yes LAR identified in "LAR Resullts 20251106"
ZN01290 | CBZZN01290PA02 | ZN1290:PA2 | LEIGHTONFIELD | Canterbury Bankstown | 57.3502 | 1 | 57.3502 | 57.3502 | 57.3502 | Villawood |  | N-1 | 2025 |  |  | 57 | 57 | 57 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN01068 | CBZZN01068PA26 | ZN1068:PA26 | LIDCOMBE | Inner West Sydney | 115.6855 | 1 | 115.6855 | 115.6855 | 115.6855 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN01068 | CBZZN01068PA27 | ZN1068:PA27 | LIDCOMBE | Inner West Sydney | 184.2548 | 1 | 184.2548 | 184.2548 | 150 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN12600 | CBZZN12600PA02 | ZN12600:PA2 | LISAROW | Lower Central Coast | 144 | 3 | 48 | 95 | 95 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12600 | CBZZN12600PA09 | ZN12600:PA9 | LISAROW | Lower Central Coast | 209 | 3 | 69.6667 | 125 | 125 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12600 | CBZZN12600PA11 | ZN12600:PA11 | LISAROW | Lower Central Coast | 88.3125 | 1 | 88.3125 | 88.3125 | 88.3125 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12600 | CBZZN12600PA03 | ZN12600:PA3 | LISAROW | Lower Central Coast | 32.726 | 1 | 32.726 | 32.726 | 32.726 | Narara |  | N-1 | 2024 |  |  | 12 | 12 | 12 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12610 | CBZZN12610PA02 | ZN12610:PA2 | LONG JETTY | Lower Central Coast | 122.6765 | 122.6765 |  | 145 | 145 | Bateau Bay |  | N-1 | 2024 |  |  | 145 | 145 | 145 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12610 | CBZZN12610PA10 | ZN12610:PA10 | LONG JETTY | Lower Central Coast | 122.6765 | 1 | 122.6765 | 122.6765 | 122.6765 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12610 | CBZZN12610PA16 | ZN12610:PA16 | LONG JETTY | Lower Central Coast | 66 | 1 | 66 | 66 | 66 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12610 | CBZZN12610PA18 | ZN12610:PA18 | LONG JETTY | Lower Central Coast | 26 | 2 | 13 | 25 | 25 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12610 | CBZZN12610PA22 | ZN12610:PA22 | LONG JETTY | Lower Central Coast | 61 | 1 | 61 | 61 | 61 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12610 | CBZZN12610PA13 | ZN12610:PA13 | LONG JETTY | Lower Central Coast | 16 | 1 | 16 | 16 | 16 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00528 | CBZZN00528PA11 | 528:83020 | MAITLAND 33 | Maitland | 19 | 1 | 19 | 19 | 19 | Largs |  | N | 2024 |  |  | 133 | 133 | 133 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00528 | CBZZN00528PA04 | 528:83019 | MAITLAND 33 | Maitland | 441.6589 | 6 | 73.6098 | 125.8808 | 125.8808 | Maitland Vale |  | N | 2024 |  |  | 240 | 240 | 240 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00528 | CBZZN00528PA13 | 528:83014 | MAITLAND 33 | Maitland | 339.0973 | 4 | 84.7743 | 114.0973 | 114.0973 | Bolwarra Heights |  | N-1 | 2024 |  |  | 193 | 193 | 193 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00528 | CBZZN00528PA07 | 528:83013 | MAITLAND 33 | Maitland | 622.2947 | 4 | 155.5737 | 191.8385 | 150 | Aberglasslyn |  | N | 2024 |  |  | 249 | 249 | 249 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00262 | CBZZN00262PA16 | ZN262:PA16 | MARRICKVILLE | Eastern Suburbs | 38 | 1 | 38 | 38 | 38 | Marrickville |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN00262 | CBZZN00262PA19 | ZN262:PA19 | MARRICKVILLE | Eastern Suburbs | 43 | 1 | 43 | 43 | 43 | Marrickville |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN00213 | CBZZN00213PA02 | 213:33773 | MARYLAND 132 | Newcastle Western Corridor | 119.5404 | 2 | 59.7702 | 66.5404 | 66.5404 | Fletcher |  | N-1 | 2024 |  |  | 67 | 67 | 67 | Existing | Under investigation
ZN00213 | CBZZN00213PA06 | 213:33769 | MARYLAND 132 | Newcastle Western Corridor | 53 | 1 | 53 | 53 | 53 | Fletcher |  | N-1 | 2024 |  |  | 53 | 53 | 53 | Existing | Under investigation
ZN00213 | CBZZN00213PA10 | 213:33777 | MARYLAND 132 | Newcastle Western Corridor | 26 | 1 | 26 | 26 | 26 | Cameron Park |  | N-1 | 2024 |  |  | 26 | 26 | 26 | Existing | Under investigation
ZN02196 | CBZZN02196PA26 | ZN2196:PA26 | MILPERRA | Canterbury Bankstown | 35 | 1 | 35 | 35 | 35 | Condell Park |  | N-1 | 2025 |  |  | 35 | 35 | 35 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN09037 | CBZZN09037PA08 | ZN9037:PA8 | MIRANDA | Sutherland | 32 | 1 | 32 | 32 | 32 | Miranda |  | N-1 | 2025 |  |  | 32 | 32 | 32 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00812 | CBZZN00812PA11 | 812:19066 | MITCHELL LINE 66 | Upper Hunter | 100.2184 | 1 | 100.2184 | 100.2184 | 100.2184 | Muswellbrook |  | N-1 | 2024 |  |  | 100 | 100 | 100 | Existing | Project under development | No LAR identfied in recent LAR Results in Nov 2025 - However switching identfied in LAR tool not practical and feeder likley to see urban growth
ZN15014 | CBZZN15014PA05 | ZN15014:PA5 | MONA VALE | Pittwater & Northern Beaches | 134 | 2 | 67 | 79 | 79 | Warriewood |  | N-1 | 2025 |  |  | 79 | 79 | 79 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN00243 | CBZZN00243PA06 | 243:80075 | MORISSET 132 | West Lake Macquarie | 262.14 | 6 | 43.69 | 64.14 | 64.14 | Wyee |  | N-1 | 2024 |  |  | 64 | 64 | 64 | Existing | Project under development
ZN10994 | CBZZN10994PA07 | ZN10994:PA7 | MORTDALE | St George | 228.9569 | 4 | 57.2392 | 69.9569 | 69.9569 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN10994 | CBZZN10994PA02 | ZN10994:PA2 | MORTDALE | St George | 37.4387 | 1 | 37.4387 | 37.4387 | 37.4387 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN10994 | CBZZN10994PA12 | ZN10994:PA12 | MORTDALE | St George | 2 | 1 | 2 | 2 | 0 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN10994 | CBZZN10994PA04 | ZN10994:PA4 | MORTDALE | St George | 72 | 1 | 72 | 72 | 72 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN00180 | CBZZN00180PA36 | ZN180:PA36 | MOSMAN | Lower North Shore | [5 empty] | Mosman |  | N-1 | 2025 |  |  | 26 | 26 | 26 |  | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN00180 | CBZZN00180PA41 | ZN180:PA41 | MOSMAN | Lower North Shore | 90 | 1 | 90 | 90 | 90 | [7 empty] | 0 | 0 |  | Check LAR | Latest N-1 results show no LAR as of Nov 2025
ZN00217 | CBZZN00217PA03 | 217:33611 | MT HUTTON | North East Lake Macquarie | [5 empty] | ELEEBANA |  | N-1 | 2025 |  |  | 53 | 53 | 53 | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00232 | CBZZN00232PA13 | 232:11457 | NELSON BAY 33 | Port Stephens | 34.3273 | 1 | 34.3273 | 34.3273 | 34.3273 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00232 | CBZZN00232PA03 | 232:33413 | NELSON BAY 33 | Port Stephens | 69.6293 | 1 | 69.6293 | 69.6293 | 69.6293 | Anna Bay |  | N-1 | 2025 |  |  | 31 | 31 | 31 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00232 | CBZZN00232PA04 | 232:11455 | NELSON BAY 33 | Port Stephens | 423.349 | 5 | 84.6698 | 110.3117 | 110.3117 | Soldiers Point |  | N-1 | 2024 |  |  | 109 | 109 | 109 |  | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00232 | CBZZN00232PA05 | 232:33409 | NELSON BAY 33 | Port Stephens | 740.4568 | 4 | 185.1142 | 257.0693 | 150 | Nelson Bay |  | N-1 | 2025 |  |  | 124 | 124 | 124 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00232 | CBZZN00232PA09 | 232:33407 | NELSON BAY 33 | Port Stephens | 6.4978 | 1 | 6.4978 | 6.4978 | 0 | Anna Bay |  | N-1 | 2025 |  |  | 183 | 183 | 183 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00210 | CBZZN00210PA12 | 210:83474 | NEW LAMBTON 33 | Newcastle Inner City | 3 | 1 | 3 | 3 | 0 | Lambton |  | N-1 | 2025 |  |  | 0 | 0 | 0 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025
ZN00202 | CBZZN00202PA30 | 202:34260 | NEWCASTLE CBD 33 | Newcastle Inner City | 146.4817 | 2 | 73.2409 | 122.6718 | 122.6718 | Bar Beach |  | N-1 | 2024 |  |  | 26 | 26 | 26 | Existing | Under investigation | Flagged by recent LAR tool run on Dev models, LAR verified, awaiting options analysis
ZN00202 | CBZZN00202PA36 | 202:34249 | NEWCASTLE CBD 33 | Newcastle Inner City | 123 | 2 | 61.5 | 79 | 79 | Newcastle West |  | N-1 | 2025 |  |  | 79 | 79 | 79 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025
ZN00524 | CBZZN00524PA05 | 524:33578 | NULKABA 33 | Greater Cessnock | 93 | 1 | 93 | 93 | 93 | Cessnock |  | N-1 | 2025 |  |  | 93 | 93 | 93 | Existing | Under investigation
ZN36000 | CBZZN36000PA04 | ZN36000:PA4 | OLYMPIC PARK | Inner West Sydney | 22 | 1 | 22 | 22 | 22 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN36000 |  | PA6 | OLYMPIC PARK | Inner West Sydney | [5 empty] | Homebush |  | N-1 | 2025 |  |  | 88 | 88 | 88 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN36000 |  | PA10 | OLYMPIC PARK | Inner West Sydney | [5 empty] | Homebush |  | N-1 | 2025 |  |  | 121 | 121 | 121 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN00342 | CBZZN00342PA33 | ZN342:PA33 | PADDINGTON | Eastern Suburbs | 12.7218 | 1 | 12.7218 | 12.7218 | 0 | Surry Hills |  | N-1 | 2025 |  |  | 13 | 13 | 13 | 2025 | Check LAR | Does not show up on the most recent LAR tool
ZN00222 | CBZZN00222PA01 | 222:33596 | PELICAN 33 | North East Lake Macquarie | 45.8016 | 1 | 45.8016 | 45.8016 | 45.8016 | BLACKSMITHS |  | N-1 | 2025 |  |  | 46 | 46 | 46 | 2025 | Under investigation | No LAR identified in "LAR Resullts 20251106" / manual Pickup check found LAR
ZN02310 | CBZZN02310PA04 | ZN2310:PA4 | PUNCHBOWL | Canterbury Bankstown | 154.3969 | 1 | 154.3969 | 154.3969 | 150 | Wiley Park |  | N-1 | 2024 |  |  | 150 | 150 | 150 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN02310 | CBZZN02310PA14 | ZN2310:PA14 | PUNCHBOWL | Canterbury Bankstown | 44 | 1 | 44 | 44 | 44 | Roselands |  | N-1 | 2025 |  |  | 44 | 44 | 44 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00239 | CBZZN00239PA10 | 239:82129 | RATHMINES 132 | West Lake Macquarie | 274 | 3 | 91.3333 | 180 | 150 | Rathmines |  | N-1 | 2024 |  |  | 180 | 180 | 180 | Existing | Under investigation
ZN00264 | CBZZN00264PA04 | 264:812 | RAYMOND TERRACE 33 | Port Stephens | [5 empty] | Raymond Terrace |  | N-1 | 2025 |  |  | 20 | 20 | 20 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00264 | CBZZN00264PA06 | 264:81236 | RAYMOND TERRACE 33 | Port Stephens | 8 | 1 | 8 | 8 | 0 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN01287 | CBZZN01287PA17 | ZN1287:PA17 | REVESBY | Canterbury Bankstown | 4 | 1 | 4 | 4 | 0 | East Hills |  | N-1 | 2025 |  |  | 4 | 4 | 4 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN01287 | CBZZN01287PA05 | ZN1287:PA5 | REVESBY | Canterbury Bankstown | 9.7062 | 1 | 9.7062 | 9.7062 | 0 | Padstow |  | N-1 | 2025 |  |  | 10 | 10 | 10 | Existing | Under investigation
ZN10995 | CBZZN10995PA07 | ZN10995:PA7 | RIVERWOOD | St George | 39 | 1 | 39 | 39 | 39 | [7 empty] | 0 | 0 |  | Check LAR | x no LAR delete
ZN36100 | CBZZN36100PA13 | ZN36100:PA13 | ROSE BAY | Eastern Suburbs | 78.497 | 1 | 78.497 | 78.497 | 78.497 | Rose Bay |  | N-1 | 2025 |  |  | 78 | 78 | 78 | 2025 | Under investigation
ZN36100 | CBZZN36100PA27 | ZN36100:PA27 | ROSE BAY | Eastern Suburbs | 45.8108 | 1 | 45.8108 | 45.8108 | 45.8108 | Vaucluse |  | N-1 | 2024 |  |  | 46 | 46 | 46 | 2025 | Check LAR | Does not show up on the most recent LAR tool
ZN00511 | CBZZN00511PA02 | 511:29873 | RUTHERFORD 33 | Maitland | 795.8218 | 5 | 159.1644 | 247.1017 | 150 | Aberglasslyn |  | N | 2024 |  |  | 396 | 396 | 396 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00511 | CBZZN00511PA03 | 511:29880 | RUTHERFORD 33 | Maitland | 7 | 1 | 7 | 7 | 0 | Rutherford |  | N-1 | 2024 |  |  | 36 | 36 | 36 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00511 | CBZZN00511PA09 | 511:29876 | RUTHERFORD 33 | Maitland | 291.5328 | 3 | 97.1776 | 109.8443 | 109.8443 | Rutherford |  | N-1 | 2024 |  |  | 151 | 151 | 151 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN03472 | CBZZN03472PA20 | ZN3472:PA20 | SEFTON | Canterbury Bankstown | 49 | 1 | 49 | 49 | 49 | Bass Hill |  | N-1 | 2025 |  |  | 49 | 49 | 49 | Existing | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00513 | CBZZN00513PA28 | 513:83500 | SINGLETON 66 | Singleton | 144.553 | 1 | 144.553 | 144.553 | 144.553 | Whittingham / Abattoir |  | N-1 | 2024 |  |  | 145 | 145 | 145 | Existing | Under investigation | Flagged by recent LAR tool run on Dev models, LAR verified, awaiting options analysis - Long term single industrial customer in rural setting
ZN14143 | CBZZN14143PA16 | ZN14143:PA16 | SOMERSBY | Lower Central Coast | [5 empty] | Kariong |  | N-1 | 2025 |  |  | 32 | 32 | 32 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN14143 | CBZZN14143PA17 | ZN14143:PA17 | SOMERSBY | Lower Central Coast | 40.0314 | 1 | 40.0314 | 40.0314 | 40.0314 | Somersby |  | N-1 | 2024 |  |  | 63 | 63 | 63 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN03154 | CBZZN03154PA03 | ZN3154:PA3 | ST IVES | Upper North Shore | 32.8657 | 1 | 32.8657 | 32.8657 | 32.8657 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN02568 | CBZZN02568PA07 | ZN2568:PA7 | ST. PETERS | Eastern Suburbs | 311.9468 | 1 | 311.9468 | 311.9468 | 150 | Newtown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA08 | ZN2568:PA8 | ST. PETERS | Eastern Suburbs | 493.7691 | 2 | 246.8845 | 302.4438 | 150 | Camperdown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA27 | ZN2568:PA27 | ST. PETERS | Eastern Suburbs | 140 | 2 | 70 | 90 | 90 | Newtown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA32 | ZN2568:PA32 | ST. PETERS | Eastern Suburbs | 19 | 1 | 19 | 19 | 19 | Erskineville |  | N-1 | 2025 |  |  | 45 | 45 | 45 | 2025 | Under investigation | LAR has been identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA19 | ZN2568:PA19 | ST. PETERS | Eastern Suburbs | 146.2911 | 1 | 146.2911 | 146.2911 | 146.2911 | Newtown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA09 | ZN2568:PA9 | ST. PETERS | Eastern Suburbs | 83 | 1 | 83 | 83 | 83 | Newtown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA20 | ZN2568:PA20 | ST. PETERS | Eastern Suburbs |  |  |  | 28 | 28 | Redfern |  | N-1 | 2025 |  |  | 28 | 28 | 28 | Existing | Under investigation | LAR has been identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA29 | ZN2568:PA29 | ST. PETERS | Eastern Suburbs | 31 | 1 | 31 | 31 | 31 | Newtown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN04853 | CBZZN04853PA26 | ZN4853:PA26 | STRATHFIELD SOUTH | Canterbury Bankstown | 7 | 1 | 7 | 7 | 0 | Strathfield South |  | N-1 | 2024 |  |  | 7 | 7 | 7 | Existing | Under investigation
ZN00901 | CBZZN00901PA22 | ZN901:PA22 | SURRY HILLS | Eastern Suburbs | 71.3839 | 1 | 71.3839 | 71.3839 | 71.3839 | Camperdown |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN00901 | CBZZN00901PA23 | ZN901:PA23 | SURRY HILLS | Eastern Suburbs | 18.065 | 1 | 18.065 | 18.065 | 18.065 | Chippendale |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN00230 | CBZZN00230PA15 | 230:814 | TANILBA BAY 33 | Port Stephens | [7 empty] | N-1 | 2025 |  |  | 200 | 200 | 200 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00230 | CBZZN00230PA12 | 230:81440 | TANILBA BAY 33 | Port Stephens | 45.4183 | 1 | 45.4183 | 45.4183 | 45.4183 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00502 | CBZZN00502PA08 | 502:48004 | TELARAH 33 | Maitland | 570.1401 | 5 | 114.028 | 144.5661 | 144.5661 | Rutherford |  | N-1 | 2024 |  |  | 156 | 156 | 156 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00502 | CBZZN00502PA07 | 502:48010 | TELARAH 33 | Maitland | 161 | 2 | 80.5 | 92 | 92 | Gillieston Heights |  | N-1 | 2024 |  |  |  | 0 | 0 |  | Check LAR | LAR due to incorrectly identified pluto at 50deg on 48009. Previous project issued to rectify.
ZN00502 | CBZZN00502PA10 | 502:48001 | TELARAH 33 | Maitland | 64.3639 | 1 | 64.3639 | 64.3639 | 64.3639 | Rutherford |  | N-1 | 2024 |  |  | 64 | 64 | 64 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00238 | CBZZN00238PA18 | 238:34136 | THORNTON 33 | Maitland | 603.8441 | 4 | 150.961 | 196 | 150 | Thornton |  | N-1 | 2024 |  |  | 196 | 196 | 196 | Existing | Project under development
ZN00238 | CBZZN00238PA20 | 238:34141 | THORNTON 33 | Maitland | 107.989 | 1 | 107.989 | 107.989 | 107.989 | Chisholm |  | N-1 | 2025 |  |  | 108 | 108 | 348 | Existing | Project in delivery
ZN00238 | CBZZN00238PA11 | 238:34151 | THORNTON 33 | Maitland | 145.2598 | 1 | 145.2598 | 145.2598 | 145.2598 | Thornton |  | N-1 | 2024 |  |  | 145 | 145 | 190 | Existing | Project in delivery
ZN00238 | CBZZN00238PA04 | 238:34148 | THORNTON 33 | Maitland | [5 empty] | Chisholm |  | N-1 | 2025 |  |  | 88 | 88 | 88 | Existing | Project in delivery | LAR identified in project to fix 34141. PI20250755.
ZN00204 | CBZZN00204PA08 | 204:82689 | TIGHES HILL | Newcastle Inner City | 171 | 1 | 171 | 171 | 150 | Mayfield East |  | N-1 | 2025 |  |  | 150 | 150 | 150 | Existing | Check LAR | No LAR identfied in recent LAR Results in Nov 2025
ZN00242 | CBZZN00242PA04 | 242:81538 | TOMAREE 33 | Port Stephens | 147.1082 | 1 | 147.1082 | 147.1082 | 147.1082 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00242 | CBZZN00242PA13 | 242:81539 | TOMAREE 33 | Port Stephens | 39 | 1 | 39 | 39 | 39 |  |  | N-1 | 2025 |  |  | 75 | 75 | 75 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN35500 | CBZZN35500PA28 | ZN35500:PA28 | TOP RYDE | Carlingford | 10 | 1 | 10 | 10 | 0 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN00270 | CBZZN00270PA08 | 270:83587 | TORONTO WEST 132 | West Lake Macquarie | 24 | 1 | 24 | 24 | 24 | Coal Point |  | N-1 | 2025 |  |  | 24 | 24 | 24 | Existing | Under investigation
ZN12640 | CBZZN12640PA08 | ZN12640:PA8 | UMINA | Lower Central Coast | 26.4984 | 1 | 26.4984 | 26.4984 | 26.4984 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12640 | CBZZN12640PA14 | ZN12640:PA14 | UMINA | Lower Central Coast | [11 empty] | 5 | 5 | 5 | 2024 | Project in delivery | Feeder added to list. LAR due to 50deg mains. Project issued to fix LV to address HV non-compliance
ZN14144 | CBZZN14144PA07 | ZN14144:PA7 | WAMBERAL | Lower Central Coast | 2 | 1 | 2 | 2 | 0 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12650 | CBZZN12650PA03 | ZN12650:PA3 | WEST GOSFORD | Lower Central Coast | [7 empty] | N-1 | 2025 |  |  | 272 | 272 | 272 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12650 | CBZZN12650PA01 | ZN12650:PA1 | WEST GOSFORD | Lower Central Coast | 87 | 1 | 87 | 87 | 87 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12650 | CBZZN12650PA06 | ZN12650:PA6 | WEST GOSFORD | Lower Central Coast | 78 | 3 | 26 | 27 | 27 | [7 empty] | 0 | 0 |  | Check LAR | No LAR identified in recent LAR Resullts in Nov 2025
ZN12650 | CBZZN12650PA12 | ZN12650:PA12 | WEST GOSFORD | Lower Central Coast | 112.7684 | 3 | 37.5895 | 71 | 71 |  |  | N-1 | 2025 |  |  | 28 | 28 | 28 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00229 | CBZZN00229PA02 | 229 | WILLIAMTOWN | Port Stephens | [7 empty] | N-1 | 2025 |  |  | 103 | 103 | 103 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00229 | CBZZN00229PA02 | 229 | WILLIAMTOWN | Port Stephens | [7 empty] | N-1 | 2025 |  |  | 121 | 121 | 121 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00229 | CBZZN00229PA04 | 229 | WILLIAMTOWN | Port Stephens | [7 empty] | N-1 | 2025 |  |  | 269 | 269 | 269 | 2025 | Project in delivery | Project Issued $1,900,000
ZN00229 | CBZZN00229PA01 | 229 | WILLIAMTOWN | Port Stephens | [7 empty] | N-1 | 2025 |  |  | 246 | 246 | 246 | 2025 | Project in delivery | Project Issued $1,900,000
ZN12660 | CBZZN12660PA06 | ZN12660:PA6 | WOY WOY | Lower Central Coast | 9 | 1 | 9 | 9 | 0 | Saratoga |  | N-1 | 2025 |  |  | 32 | 32 | 32 | Existing | Under investigation | LAR identified in recent LAR results Nov 2025
ZN14891 | CBZZN14891PA01 | ZN14891:PA1 | WYONG | Upper Central Coast | 58 | 1 | 58 | 58 | 58 | KANWAL |  | N-1 | 2024 |  |  | 58 | 58 | 58 | 2024 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA10 | ZN14891:PA10 | WYONG | Upper Central Coast | 329.9397 | 4 | 82.4849 | 216.415 | 150 | TACOMA |  | N-1 | 2024 |  |  | 216.415 | 216 | 216 | 2024 | Project under development | Yes LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA16 | ZN14891:PA16 | WYONG | Upper Central Coast | 770.7866 | 5 | 154.1573 | 220 | 150 | WYONGAH |  | N-1 | 2024 |  |  | 220 | 220 | 220 | 2024 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA17 | ZN14891:PA17 | WYONG | Upper Central Coast | 166.5002 | 2 | 83.2501 | 147.5002 | 147.5002 | HAMLYN TERRACE |  | N-1 | 2025 |  |  | 147.5002 | 148 | 148 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA05 | ZN14891:PA5 | WYONG | Upper Central Coast | 371.8812 | 8 | 46.4851 | 76.4993 | 76.4993 | JILLIBY |  | N-1 | 2024 |  |  | 76.4993 | 76 | 76 | 2024 | Project under development | Yes LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA12 | ZN14891:PA12 | WYONG | Upper Central Coast | 208.9081 | 3 | 69.636 | 74.248 | 74.248 | WYONG CREEK |  | N-1 | 2024 |  |  | 74.248 | 74 | 74 | 2024 | Project under development | Yes LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA21 | ZN14891:PA21 | WYONG | Upper Central Coast | 26 | 1 | 26 | 26 | 26 | WALLARAH |  | N-1 | 2025 |  |  | 26 | 26 | 26 | 2025 | Check LAR | No LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA21 | ZN14891:PA03 | WYONG | Upper Central Coast | [5 empty] | WARNERVALE |  | N-1 | 2025 |  | 68 | 167 | 167 | 167 | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN14891 | CBZZN14891PA21 | ZN14891:PA14 | WYONG | Upper Central Coast | [5 empty] | JILLIBY |  | N-1 | 2025 |  |  | 217 | 217 | 217 | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00188 | CBZZN00188PA43 | ZN188:PA43 | ZETLAND | Eastern Suburbs | 42.8249 | 1 | 42.8249 | 42.8249 | 42.8249 | Chippendale |  | N-1 | 2025 |  |  | 0 | 0 | 0 | 2025 | Check LAR | No LAR identified in Dev model in LAR Tool Nov 2025 results
ZN00188 | CBZZN00188PA10 | ZN188:PA10 | ZETLAND | Eastern Suburbs |  |  |  | 26 | 26 | Waterloo |  | N-1 | 2025 |  |  | 26 | 26 | 26 | 2025 | Project under development | LAR project has been written, awaiting approval PI2025_1187.
ZN00204 | CBZZN00204PA17 | 204:82689 | TIGHES HILL | Newcastle Inner City |  |  |  | 38 | 38 | Broadmeadow |  | N-1 | 2025 |  |  | 38 | 38 | 38 | Existing | Project under development | Commercial business district spur (Beaumont St) with LAR
ZN00204 | CBZZN00204PA09 | 204:82691 | TIGHES HILL | Newcastle Inner City |  |  |  | 47 | 47 | Tighes Hill / Islington |  | N-1 | 2025 |  |  | 47 | 47 | 47 | 2026 | Project under development | LAR identified in recent LAR results Nov 2025
Please add any feeders that have LAR where there is a project

## 2025 DTAPR CUT 1 (hidden)
Zone | Panel |  | Panel OMS | Zone | Area Plan | Max LAR All | Max LAR (Capped at 150) | Location | Location | Feeder Name | Type of risk | Year Identified | Rating (Amps) | 2024/25 Load (11kV amps) | 25/26 Load at Risk (11kV Amps) | 26/27 Load at Risk (11kV Amps) | 27/28 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution | Comments | Please update green
ZN00224 | CBZZN00224PA11 | PA11 | 224:80346 | ARGENTON 132/11 | Newcastle Western Corridor | 178.6974 | 150 | Speers Point | Speers Point | ARGENTON 132/11 PA11 | N-1 | 2024 |  |  | 179 | 179 | 179 | Existing | Under investigation
ZN12570 | CBZZN12570PA24 | PA24 | ZN12570:PA24 | AVOCA | Lower Central Coast | 164 | 150 | MacMasters Beach | Macmasters Beach | AVOCA PA24 | N-1 | 2024 |  |  | 45 | 45 | 45 | 2024 | Under investigation | LAR identified as much lower in recent LAR results Nov 2025
ZN12570 | CBZZN12570PA33 | PA33 | ZN12570:PA33 | AVOCA | Lower Central Coast | 60.6129 | 60.6129 | MacMasters Beach | Macmasters Beach | AVOCA PA33 | N-1 | 2024 |  |  | 21 | 21 | 21 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN35800 | CBZZN35800PA10 | PA10 | ZN35800:PA10 | BANKSTOWN | Canterbury Bankstown | 50 | 50 | Punchbowl | Punchbowl | BANKSTOWN PA10 | N-1 | 2025 |  |  | 50 | 50 | 50 | Existing | Under investigation
ZN02400 | CBZZN02400PA11 | PA11 | ZN2400:PA11 | BEROWRA | North West Sydney | 32 | 32 | Brooklyn / Somersby | Brooklyn / Somersby | BEROWRA PA11 | N-1 | 2025 |  |  | 32 | 32 | 32 | 2025 | Project in delivery | Project initiated to loop in FDR with Somersby Zn PA17.
ZN02400 | CBZZN02400PA21 | PA21 | ZN2400:PA21 | BEROWRA | North West Sydney | 104 | 104 | Cowan | Cowan | BEROWRA PA21 | N-1 | 2025 |  |  | 104 | 104 | 104 | 2025 | Under investigation | Assoc. with the above project (PA11). When Proj. completed, being able to move approx. 97A (PA11, CP2715) to Somersby PA17 will fix this problem.
ZN10991 | CBZZN10991PA01 | PA1 | ZN10991:PA1 | BLAKEHURST | St George | 90.7146 | 90.7146 | Blakehurst | Blakehurst | BLAKEHURST PA1 | N-1 | 2025 |  |  | 156 | 156 | 156 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR unverified
ZN10991 | CBZZN10991PA12 | PA12 | ZN10991:PA12 | BLAKEHURST | St George | 69 | 69 | Blakehurst | Blakehurst | BLAKEHURST PA12 | N-1 | 2025 |  |  | 90 | 90 | 90 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR unverified
ZN00512 | CBZZN00512PA13 | PA13 | 512:83736 | BRANXTON 66 | Singleton | 85.0566 | 85.0566 | Branxton | Branxton | BRANXTON 66 PA13 | N-1 | 2024 |  |  | 85 | 85 | 85 | Existing | Project under development | Flagged by recent LAR tool run on Dev models, LAR verified, awaiting options analysis
ZN02835 |  | PA9 | PA9 | BURWOOD | Inner West Sydney |  |  | Burwood | Burwood | BURWOOD PA9 | N-1 | 2025 |  |  | 53 | 53 | 53 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR verified, awaiting options analysis
ZN02835 |  | PA19 | PA19 | BURWOOD | Inner West Sydney |  |  | Canada Bay | Canada Bay | BURWOOD PA19 | N-1 | 2025 |  |  | 136 | 136 | 136 | 2025 | Under investigation | Flagged by recent LAR tool run on dev models, LAR verified, awaiting options analysis
ZN00214 | CBZZN00214PA01 | PA1 | 214:8666 | CARDIFF 33 | Newcastle Western Corridor | 46 | 46 | Cardiff | Cardiff | CARDIFF 33 PA1 | N-1 | 2025 |  |  | 46 | 46 | 46 | Existing | Under investigation
ZN00214 | CBZZN00214PA12 | PA12 | 214:8670 | CARDIFF 33 | Newcastle Western Corridor | 22 | 22 | Warners Bay | Warners Bay | CARDIFF 33 PA12 | N-1 | 2025 |  |  | 22 | 22 | 22 | Existing | Under investigation
ZN00214 | CBZZN00214PA16 | PA16 | 214:8665 | CARDIFF 33 | Newcastle Western Corridor | 80 | 80 | Cardiff | Cardiff | CARDIFF 33 PA16 | N-1 | 2025 |  |  | 80 | 80 | 80 | Existing | Under investigation
ZN00522 | CBZZN00522PA02 | PA2 | 522:83123 | CESSNOCK SOUTH | Greater Cessnock | 179.6087 | 150 | Cessnock | Cessnock | CESSNOCK SOUTH PA2 | N-1 | 2024 |  |  | 180 | 180 | 180 | Existing | Under investigation
ZN00522 | CBZZN00522PA07 | PA7 | 522:83129 | CESSNOCK SOUTH | Greater Cessnock | 60 | 60 | Cessnock | Cessnock | CESSNOCK SOUTH PA7 | N-1 | 2025 |  |  | 60 | 60 | 60 | Existing | Under investigation
ZN00261 | CBZZN00261PA08 | PA8 | 261:81879 | CHARLESTOWN 132 | North East Lake Macquarie | 119 | 119 | CHARLESTOWN | Charlestown | CHARLESTOWN 132 PA8 | N-1 | 2025 |  |  | 119 | 119 | 119 | 2025 | Under investigation | No LAR identified in "LAR Resullts 20251106", suspect issues trunks loaded 93%
ZN14892 | CBZZN14892PA01 | PA1 | ZN14892:PA1 | CHARMHAVEN | Upper Central Coast | 38 | 38 | WOONGARRAH | Woongarrah | CHARMHAVEN PA1 | N-1 | 2024 |  |  | 38 | 38 | 38 | 2024 | Project in delivery | LAR was identified in "LAR Resullts 20251106" project issued new PA20R $1,566,000
ZN14892 | CBZZN14892PA13 | PA13 | ZN14892:PA09 | CHARMHAVEN | Upper Central Coast |  |  | HAMLYN TERRACE | Hamlyn Terrace | CHARMHAVEN PA13 | N-1 | 2025 |  |  | 104 |  |  | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN14892 | CBZZN14892PA13 | PA13 | ZN14892:PA10 | CHARMHAVEN | Upper Central Coast |  |  | WOONGARRAH | Woongarrah | CHARMHAVEN PA13 | N-1 | 2025 |  |  | 66 |  |  | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN14892 | CBZZN14892PA13 | PA13 | ZN14892:PA12 | CHARMHAVEN | Upper Central Coast |  |  | WOONGARRAH | Woongarrah | CHARMHAVEN PA13 | N-1 | 2025 |  |  | 120 |  |  | 2025 | Project in delivery | LAR was identified in "LAR Resullts 20251106" project issued new PA20R $1,566,000 | NEW ROW ADDED
ZN00080 | CBZZN00080PA37 | PA37 | ZN80:PA37 | CHATSWOOD | Lower North Shore |  |  | Lane Cove | Lane Cove | CHATSWOOD PA37 | N-1 | 2025 |  |  | 194 | 194 | 194 | 2025 | Project under development | Latest N-1 results identified this feeder as an N-1 LAR issue as of 7 Nov 2025. PI-2025_1193 is investigating possible solutions.
ZN00080 | CBZZN00080PA40 | PA40 | ZN80:PA40 | CHATSWOOD | Lower North Shore |  |  | Lane Cove | Lane Cove | CHATSWOOD PA40 | N-1 | 2025 |  |  | 110 | 110 | 110 | 2025 | Project under development | Latest N-1 results identified this feeder as an N-1 LAR issue as of 7 Nov 2025. PI-2025_1193 is investigating possible solutions.
ZN00874 | CBZZN00874PA04 | PA4 | ZN874:PA4 | CONCORD | Inner West Sydney | 65 | 65 | Breakfast Point | Breakfast Point | CONCORD PA4 | N-1 | 2021 |  |  | 119 | 119 | 119 | 2021 | Project in delivery | PI-2021_1339
ZN00874 |  | PA17 | PA17 | CONCORD | Inner West Sydney |  |  | Breakfast Point | Breakfast Point | CONCORD PA17 | N-1 | 2021 |  |  | 165 | 165 | 165 | 2021 | Project in delivery | PI-2021_1339
ZN00874 |  | PA18 | PA18 | CONCORD | Inner West Sydney |  |  | Breakfast Point | Breakfast Point | CONCORD PA18 | N-1 | 2021 |  |  | 79 | 79 | 79 | 2021 | Project in delivery | PI-2021_1339
ZN00874 |  | PA22 | PA22 | CONCORD | Inner West Sydney |  |  | Breakfast Point | Breakfast Point | CONCORD PA22 | N-1 | 2021 |  |  | 135 | 135 | 135 | 2021 | Project in delivery | PI-2021_1339
ZN00206 | CBZZN00206PA01 | PA1 | 206:34441 | CROUDANCE BAY | North East Lake Macquarie |  |  | WARNERS BAY | Warners Bay | CROUDANCE BAY PA1 | N-1 | 2025 |  |  | 196 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00206 | CBZZN00206PA02 | PA2 | 206:34438 | CROUDANCE BAY | North East Lake Macquarie |  |  | VALENTINE | Valentine | CROUDANCE BAY PA2 | N-1 | 2025 |  |  | 69 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00206 | CBZZN00206PA06 | PA6 | 206:34432 | CROUDANCE BAY | North East Lake Macquarie |  |  | BELMONT | Belmont | CROUDANCE BAY PA6 | N-1 | 2025 |  |  | 104 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00206 | CBZZN00206PA12 | PA12 | 206:34434 | CROUDANCE BAY | North East Lake Macquarie |  |  | VALENTINE | Valentine | CROUDANCE BAY PA12 | N-1 | 2025 |  |  | 206 |  |  | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN07481 | CBZZN07481PA09 | PA9 | ZN7481:PA9 | DARLING HARBOUR 132/11kV | Camperdown & Blackwattle Bay | 299.3672 | 150 | Pyrmont | Pyrmont | DARLING HARBOUR 132/11kV PA9 | N-1 | 2025 |  |  | 40 | 40 | 40 | 2025 | Project in delivery | LAR. Project has been issued under PI2025_1138.
ZN00216 | CBZZN00216PA09 | PA9 | 216:10729 | EDGEWORTH 33 | Newcastle Western Corridor | 99.6071 | 99.6071 | Cameron Park | Cameron Park | EDGEWORTH 33 PA9 | N-1 | 2024 |  |  | 100 | 100 | 100 | Existing | Under investigation
ZN00216 | CBZZN00216PA10 | PA10 | 216:10722 | EDGEWORTH 33 | Newcastle Western Corridor | 108.4778 | 108.4778 | Holmesville | Holmesville | EDGEWORTH 33 PA10 | N-1 | 2024 |  |  | 108 | 108 | 108 | Existing | Under investigation
ZN00216 | CBZZN00216PA01 | PA1 | 216:10724 | EDGEWORTH 33 | Newcastle Western Corridor | 50.508 | 50.508 | Cameron Park | Cameron Park | EDGEWORTH 33 PA1 | N-1 | 2024 |  |  | 51 | 51 | 51 | Existing | Under investigation
ZN00216 | CBZZN00216PA07 | PA7 | 216:10728 | EDGEWORTH 33 | Newcastle Western Corridor | 41 | 41 | Cameron Park | Cameron Park | EDGEWORTH 33 PA7 | N-1 | 2025 |  |  | 41 | 41 | 41 | Existing | Under investigation
ZN36200 | CBZZN36200PA08 | PA8 | ZN36200:PA8 | EMPIRE BAY | Lower Central Coast | 31.7519 | 31.7519 | Kilcare | Kilcare | EMPIRE BAY PA8 | N-1 | 2024 |  |  | 87 | 87 | 87 |  | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12580 | CBZZN12580PA13 | PA13 | ZN12580:PA13 | ERINA | Lower Central Coast | 35 | 35 | Erina | Erina | ERINA PA13 | N-1 | 2025 |  |  | 35 | 35 | 35 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12580 | CBZZN12580PA07 | PA7 | ZN12580:PA7 | ERINA | Lower Central Coast | 123 | 123 | Erina | Erina | ERINA PA7 | N-1 | 2025 |  |  | 123 | 123 | 123 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12580 | CBZZN12580PA01 | PA1 | ZN12580:PA1 | ERINA | Lower Central Coast | 8 | 0 | Green Point | Green Point | ERINA PA1 | N-1 | 2025 |  |  | 33 | 33 | 33 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN02466 |  | PA4 | PA4 | FLEMINGTON | Inner West Sydney |  |  | Homebush | Homebush | FLEMINGTON PA4 | N-1 | 2025 |  |  | 175 | 175 | 175 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN00129 | CBZZN00129PA36 | PA36 | ZN129:PA36 | HUNTERS HILL | Carlingford |  |  | Putney | Putney | HUNTERS HILL PA36 | N-1 | 2025 |  |  | 50 | 50 | 50 | 2025 | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN00129 | CBZZN00129PA41 | PA41 | ZN129:PA41 | HUNTERS HILL | Carlingford | 37.9192 | 37.9192 | Riverview | Riverview | HUNTERS HILL PA41 | N-1 | 2025 |  |  | 47 | 47 | 47 | Existing | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN00129 | CBZZN00129PA57 | PA57 | ZN129:PA57 | HUNTERS HILL | Carlingford |  |  | Riverview | Riverview | HUNTERS HILL PA57 | N-1 | 2025 |  |  | 38 | 38 | 38 | 2025 | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN09252 | CBZZN09252PA25 | PA25 | ZN9252:PA25 | JANNALI | Sutherland | 152 | 150 | Woronora | Woronora | JANNALI PA25 | N-1 | 2025 |  |  | 150 | 150 | 150 | Existing | Under investigation
ZN00507 | CBZZN00507PA06 | PA6 | 507:80932 | KURRI 132/11kV | Greater Cessnock | 162 | 150 | Kurri Kurri | Kurri Kurri | KURRI 132/11kV PA6 | N-1 | 2024 |  |  | 162 | 162 | 162 | Existing | Under investigation
ZN00507 | CBZZN00507PA12 | PA12 | 507:80914 | KURRI 132/11kV | Greater Cessnock | 50 | 50 | Heddon Greta | Heddon Greta | KURRI 132/11kV PA12 | N-1 | 2025 |  |  | 50 | 50 | 50 | Existing | Under investigation
ZN00507 | CBZZN00507PA19 | PA19 | 507:80923 | KURRI 132/11kV | Greater Cessnock | 114.5858 | 114.5858 | Gillieston Heights | Gillieston Heights | KURRI 132/11kV PA19 | N-1 | 2024 |  |  | 115 | 115 | 115 | Existing | Under investigation
ZN13000 | CBZZN13000PA07 | PA7 | ZN13000:PA7 | LAKE MUNMORAH | Upper Central Coast | 152.3997 | 150 | SUMMERLAND POINT | Summerland Point | LAKE MUNMORAH PA7 | N-1 | 2024 |  |  | 152.3997 | 152 | 152 | 2024 | Under investigation | Yes LAR identified in "LAR Resullts 20251106"
ZN12610 | CBZZN12610PA02 | PA2 | ZN12610:PA2 | LONG JETTY | Lower Central Coast | 145 | 145 | Bateau Bay | Bateau Bay | LONG JETTY PA2 | N-1 | 2024 |  |  | 145 | 145 | 145 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00528 | CBZZN00528PA11 | PA11 | 528:83020 | MAITLAND 33 | Maitland | 19 | 19 | Largs | Largs | MAITLAND 33 PA11 | N | 2024 |  |  | 133 | 133 | 133 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00528 | CBZZN00528PA04 | PA4 | 528:83019 | MAITLAND 33 | Maitland | 125.8808 | 125.8808 | Maitland Vale | Maitland Vale | MAITLAND 33 PA4 | N | 2024 |  |  | 240 | 240 | 240 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00528 | CBZZN00528PA13 | PA13 | 528:83014 | MAITLAND 33 | Maitland | 114.0973 | 114.0973 | Bolwarra Heights | Bolwarra Heights | MAITLAND 33 PA13 | N-1 | 2024 |  |  | 193 | 193 | 193 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00528 | CBZZN00528PA07 | PA7 | 528:83013 | MAITLAND 33 | Maitland | 191.8385 | 150 | Aberglasslyn | Aberglasslyn | MAITLAND 33 PA7 | N | 2024 |  |  | 249 | 249 | 249 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00213 | CBZZN00213PA02 | PA2 | 213:33773 | MARYLAND 132 | Newcastle Western Corridor | 66.5404 | 66.5404 | Fletcher | Fletcher | MARYLAND 132 PA2 | N-1 | 2024 |  |  | 67 | 67 | 67 | Existing | Under investigation
ZN00213 | CBZZN00213PA06 | PA6 | 213:33769 | MARYLAND 132 | Newcastle Western Corridor | 53 | 53 | Fletcher | Fletcher | MARYLAND 132 PA6 | N-1 | 2024 |  |  | 53 | 53 | 53 | Existing | Under investigation
ZN00213 | CBZZN00213PA10 | PA10 | 213:33777 | MARYLAND 132 | Newcastle Western Corridor | 26 | 26 | Cameron Park | Cameron Park | MARYLAND 132 PA10 | N-1 | 2024 |  |  | 26 | 26 | 26 | Existing | Under investigation
ZN00812 | CBZZN00812PA11 | PA11 | 812:19066 | MITCHELL LINE 66 | Upper Hunter | 100.2184 | 100.2184 | Muswellbrook | Muswellbrook | MITCHELL LINE 66 PA11 | N-1 | 2024 |  |  | 100 | 100 | 100 | Existing | Project under development | No LAR identfied in recent LAR Results in Nov 2025 - However switching identfied in LAR tool not practical and feeder likley to see urban growth
ZN00243 | CBZZN00243PA06 | PA6 | 243:80075 | MORISSET 132 | West Lake Macquarie | 64.14 | 64.14 | Wyee | Wyee | MORISSET 132 PA6 | N-1 | 2024 |  |  | 64 | 64 | 64 | Existing | Project under development
ZN00180 | CBZZN00180PA36 | PA36 | ZN180:PA36 | MOSMAN | Lower North Shore |  |  | Mosman | Mosman | MOSMAN PA36 | N-1 | 2025 |  |  | 26 | 26 | 26 |  | Under investigation | Latest N-1 results identified this feeder as an N-1 LAR issue as of Nov 2025
ZN00217 | CBZZN00217PA03 | PA3 | 217:33611 | MT HUTTON | North East Lake Macquarie |  |  | ELEEBANA | Eleebana | MT HUTTON PA3 | N-1 | 2025 |  |  | 53 | 53 | 53 | 2025 | Under investigation | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00232 | CBZZN00232PA03 | PA3 | 232:33413 | NELSON BAY 33 | Port Stephens | 69.6293 | 69.6293 | Anna Bay | Anna Bay | NELSON BAY 33 PA3 | N-1 | 2025 |  |  | 31 | 31 | 31 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00232 | CBZZN00232PA04 | PA4 | 232:11455 | NELSON BAY 33 | Port Stephens | 110.3117 | 110.3117 | Soldiers Point | Soldiers Point | NELSON BAY 33 PA4 | N-1 | 2024 |  |  | 109 | 109 | 109 |  | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00232 | CBZZN00232PA05 | PA5 | 232:33409 | NELSON BAY 33 | Port Stephens | 257.0693 | 150 | Nelson Bay | Nelson Bay | NELSON BAY 33 PA5 | N-1 | 2025 |  |  | 124 | 124 | 124 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00232 | CBZZN00232PA09 | PA9 | 232:33407 | NELSON BAY 33 | Port Stephens | 6.4978 | 0 | Anna Bay | Anna Bay | NELSON BAY 33 PA9 | N-1 | 2025 |  |  | 183 | 183 | 183 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00202 | CBZZN00202PA30 | PA30 | 202:34260 | NEWCASTLE CBD 33 | Newcastle Inner City | 122.6718 | 122.6718 | Bar Beach | Bar Beach | NEWCASTLE CBD 33 PA30 | N-1 | 2024 |  |  | 26 | 26 | 26 | Existing | Under investigation | Flagged by recent LAR tool run on Dev models, LAR verified, awaiting options analysis
ZN00524 | CBZZN00524PA05 | PA5 | 524:33578 | NULKABA 33 | Greater Cessnock | 93 | 93 | Cessnock | Cessnock | NULKABA 33 PA5 | N-1 | 2025 |  |  | 93 | 93 | 93 | Existing | Under investigation
ZN36000 |  | PA6 | PA6 | OLYMPIC PARK | Inner West Sydney |  |  | Homebush | Homebush | OLYMPIC PARK PA6 | N-1 | 2025 |  |  | 88 | 88 | 88 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN36000 |  | PA10 | PA10 | OLYMPIC PARK | Inner West Sydney |  |  | Homebush | Homebush | OLYMPIC PARK PA10 | N-1 | 2025 |  |  | 121 | 121 | 121 | 2025 | Project under development | Flagged by recent LAR tool run on dev models, LAR verified, project under development
ZN00222 | CBZZN00222PA01 | PA1 | 222:33596 | PELICAN 33 | North East Lake Macquarie | 45.8016 | 45.8016 | BLACKSMITHS | Blacksmiths | PELICAN 33 PA1 | N-1 | 2025 |  |  | 46 | 46 | 46 | 2025 | Under investigation | No LAR identified in "LAR Resullts 20251106" / manual Pickup check found LAR
ZN00239 | CBZZN00239PA10 | PA10 | 239:82129 | RATHMINES 132 | West Lake Macquarie | 180 | 150 | Rathmines | Rathmines | RATHMINES 132 PA10 | N-1 | 2024 |  |  | 180 | 180 | 180 | Existing | Under investigation
ZN00264 | CBZZN00264PA04 | PA4 | 264:812 | RAYMOND TERRACE 33 | Port Stephens |  |  | Raymond Terrace | Raymond Terrace | RAYMOND TERRACE 33 PA4 | N-1 | 2025 |  |  | 20 | 20 | 20 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN36100 | CBZZN36100PA13 | PA13 | ZN36100:PA13 | ROSE BAY | Eastern Suburbs | 78.497 | 78.497 | Rose Bay | Rose Bay | ROSE BAY PA13 | N-1 | 2025 |  |  | 78 | 78 | 78 | 2025 | Under investigation
ZN00511 | CBZZN00511PA02 | PA2 | 511:29873 | RUTHERFORD 33 | Maitland | 247.1017 | 150 | Aberglasslyn | Aberglasslyn | RUTHERFORD 33 PA2 | N | 2024 |  |  | 396 | 396 | 396 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00511 | CBZZN00511PA03 | PA3 | 511:29880 | RUTHERFORD 33 | Maitland | 7 | 0 | Rutherford | Rutherford | RUTHERFORD 33 PA3 | N-1 | 2024 |  |  | 36 | 36 | 36 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00511 | CBZZN00511PA09 | PA9 | 511:29876 | RUTHERFORD 33 | Maitland | 109.8443 | 109.8443 | Rutherford | Rutherford | RUTHERFORD 33 PA9 | N-1 | 2024 |  |  | 151 | 151 | 151 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00513 | CBZZN00513PA28 | PA28 | 513:83500 | SINGLETON 66 | Singleton | 144.553 | 144.553 | Whittingham / Abattoir | Whittingham / Abattoir | SINGLETON 66 PA28 | N-1 | 2024 |  |  | 145 | 145 | 145 | Existing | Under investigation | Flagged by recent LAR tool run on Dev models, LAR verified, awaiting options analysis - Long term single industrial customer in rural setting
ZN14143 | CBZZN14143PA16 | PA16 | ZN14143:PA16 | SOMERSBY | Lower Central Coast |  |  | Kariong | Kariong | SOMERSBY PA16 | N-1 | 2025 |  |  | 32 | 32 | 32 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN14143 | CBZZN14143PA17 | PA17 | ZN14143:PA17 | SOMERSBY | Lower Central Coast | 40.0314 | 40.0314 | Somersby | Somersby | SOMERSBY PA17 | N-1 | 2024 |  |  | 63 | 63 | 63 | 2024 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN02568 | CBZZN02568PA32 | PA32 | ZN2568:PA32 | ST. PETERS | Eastern Suburbs | 19 | 19 | Erskineville | Erskineville | ST. PETERS PA32 | N-1 | 2025 |  |  | 45 | 45 | 45 | 2025 | Under investigation | LAR has been identified in Dev model in LAR Tool Nov 2025 results
ZN02568 | CBZZN02568PA20 | PA20 | ZN2568:PA20 | ST. PETERS | Eastern Suburbs | 28 | 28 | Redfern | Redfern | ST. PETERS PA20 | N-1 | 2025 |  |  | 28 | 28 | 28 | Existing | Under investigation | LAR has been identified in Dev model in LAR Tool Nov 2025 results
ZN00230 | CBZZN00230PA15 | PA15 | 230:814 | TANILBA BAY 33 | Port Stephens |  |  | Tanilba Bay | Tanilba Bay | TANILBA BAY 33 PA15 | N-1 | 2025 |  |  | 200 | 200 | 200 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00502 | CBZZN00502PA08 | PA8 | 502:48004 | TELARAH 33 | Maitland | 144.5661 | 144.5661 | Rutherford | Rutherford | TELARAH 33 PA8 | N-1 | 2024 |  |  | 156 | 156 | 156 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00502 | CBZZN00502PA10 | PA10 | 502:48001 | TELARAH 33 | Maitland | 64.3639 | 64.3639 | Rutherford | Rutherford | TELARAH 33 PA10 | N-1 | 2024 |  |  | 64 | 64 | 64 | Existing | Project under development | LAR investigated. Project drafted to rectify
ZN00238 | CBZZN00238PA18 | PA18 | 238:34136 | THORNTON 33 | Maitland | 196 | 150 | Thornton | Thornton | THORNTON 33 PA18 | N-1 | 2024 |  |  | 196 | 196 | 196 | Existing | Project under development
ZN00238 | CBZZN00238PA20 | PA20 | 238:34141 | THORNTON 33 | Maitland | 107.989 | 107.989 | Chisholm | Chisholm | THORNTON 33 PA20 | N-1 | 2025 |  |  | 108 | 108 | 348 | Existing | Project in delivery
ZN00238 | CBZZN00238PA11 | PA11 | 238:34151 | THORNTON 33 | Maitland | 145.2598 | 145.2598 | Thornton | Thornton | THORNTON 33 PA11 | N-1 | 2024 |  |  | 145 | 145 | 190 | Existing | Project in delivery
ZN00238 | CBZZN00238PA04 | PA4 | 238:34148 | THORNTON 33 | Maitland |  |  | Chisholm | Chisholm | THORNTON 33 PA4 | N-1 | 2025 |  |  | 88 | 88 | 88 | Existing | Project in delivery | LAR identified in project to fix 34141. PI20250755.
ZN00242 | CBZZN00242PA13 | PA13 | 242:81539 | TOMAREE 33 | Port Stephens | 39 | 39 | Nelson Bay | Nelson Bay | TOMAREE 33 PA13 | N-1 | 2025 |  |  | 75 | 75 | 75 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00270 | CBZZN00270PA08 | PA8 | 270:83587 | TORONTO WEST 132 | West Lake Macquarie | 24 | 24 | Coal Point | Coal Point | TORONTO WEST 132 PA8 | N-1 | 2025 |  |  | 24 | 24 | 24 | Existing | Under investigation
ZN12650 | CBZZN12650PA03 | PA3 | ZN12650:PA3 | WEST GOSFORD | Lower Central Coast |  |  | Gosford | Gosford | WEST GOSFORD PA3 | N-1 | 2025 |  |  | 272 | 272 | 272 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN12650 | CBZZN12650PA12 | PA12 | ZN12650:PA12 | WEST GOSFORD | Lower Central Coast | 71 | 71 | Gosford | Gosford | WEST GOSFORD PA12 | N-1 | 2025 |  |  | 28 | 28 | 28 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00229 | CBZZN00229PA02 | PA2 | 34986 | WILLIAMTOWN | Port Stephens |  |  | Fern Bay | Fern Bay | WILLIAMTOWN PA2 | N-1 | 2025 |  |  | 103 | 103 | 103 | 2025 | Under investigation | LAR identified in recent LAR results Nov 2025
ZN00229 | CBZZN00229PA04 | PA4 | 34992 | WILLIAMTOWN | Port Stephens |  |  | Williamtown | Williamtown | WILLIAMTOWN PA4 | N-1 | 2025 |  |  | 269 | 269 | 269 | 2025 | Project in delivery | Project Issued $1,900,000
ZN00229 | CBZZN00229PA01 | PA1 | 34983 | WILLIAMTOWN | Port Stephens |  |  | Williamtown | Williamtown | WILLIAMTOWN PA1 | N-1 | 2025 |  |  | 246 | 246 | 246 | 2025 | Project in delivery | Project Issued $1,900,000
ZN12660 | CBZZN12660PA06 | PA6 | ZN12660:PA6 | WOY WOY | Lower Central Coast | 9 | 0 | Saratoga | Saratoga | WOY WOY PA6 | N-1 | 2025 |  |  | 32 | 32 | 32 | Existing | Under investigation | LAR identified in recent LAR results Nov 2025
ZN14891 | CBZZN14891PA10 | PA10 | ZN14891:PA10 | WYONG | Upper Central Coast | 216.415 | 150 | TACOMA | Tacoma | WYONG PA10 | N-1 | 2024 |  |  | 216.415 | 216 | 216 | 2024 | Project under development | Yes LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA05 | PA5 | ZN14891:PA5 | WYONG | Upper Central Coast | 76.4993 | 76.4993 | JILLIBY | Jilliby | WYONG PA5 | N-1 | 2024 |  |  | 76.4993 | 76 | 76 | 2024 | Project under development | Yes LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA12 | PA12 | ZN14891:PA12 | WYONG | Upper Central Coast | 74.248 | 74.248 | WYONG CREEK | Wyong Creek | WYONG PA12 | N-1 | 2024 |  |  | 74.248 | 74 | 74 | 2024 | Project under development | Yes LAR identified in "LAR Resullts 20251106"
ZN14891 | CBZZN14891PA21 | PA21 | ZN14891:PA03 | WYONG | Upper Central Coast |  |  | WARNERVALE | Warnervale | WYONG PA21 | N-1 | 2025 |  | 68 | 167 | 167 | 167 | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN14891 | CBZZN14891PA21 | PA21 | ZN14891:PA14 | WYONG | Upper Central Coast |  |  | JILLIBY | Jilliby | WYONG PA21 | N-1 | 2025 |  |  | 217 | 217 | 217 | 2025 | Project under development | Yes LAR identified in "LAR Resullts 20251106" | NEW ROW ADDED
ZN00188 | CBZZN00188PA10 | PA10 | ZN188:PA10 | ZETLAND | Eastern Suburbs | 26 | 26 | Waterloo | Waterloo | ZETLAND PA10 | N-1 | 2025 |  |  | 26 | 26 | 26 | 2025 | Project under development | LAR project has been written, awaiting approval PI2025_1187.
ZN00204 | CBZZN00204PA17 | PA17 | 204:82689 | TIGHES HILL | Newcastle Inner City | 38 | 38 | Broadmeadow | Broadmeadow | TIGHES HILL PA17 | N-1 | 2025 |  |  | 38 | 38 | 38 | Existing | Project under development | Commercial business district spur (Beaumont St) with LAR
ZN00204 | CBZZN00204PA09 | PA9 | 204:82691 | TIGHES HILL | Newcastle Inner City | 47 | 47 | Tighes Hill / Islington | Tighes Hill / Islington | TIGHES HILL PA9 | N-1 | 2025 |  |  | 47 | 47 | 47 | 2026 | Project under development | LAR identified in recent LAR results Nov 2025

## 2025 DTAPR CUT 2 (hidden)
Location | Feeder Name | Type of risk | Year Identified | Rating (Amps) | 2024/25 Load (11kV amps) | 25/26 N-1 Load at Risk (11kV Amps) | 26/27 N-1 Load at Risk (11kV Amps) | 27/28 N-1 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution
Speers Point | ARGENTON 132/11 PA11 | N-1 | 2024 | 400 | 322 | 179 | 179 | 179 | Existing | Under investigation | 322
Macmasters Beach | AVOCA PA24 | N-1 | 2024 | 280 | 158 | 45 | 45 | 45 | Existing | Under investigation | 158
Macmasters Beach | AVOCA PA33 | N-1 | 2024 | 325 | 156 | 21 | 21 | 21 | Existing | Under investigation | 156
Punchbowl | BANKSTOWN PA10 | N-1 | 2025 | 300 | 174 | 50 | 50 | 50 | Existing | Under investigation | 174
Brooklyn / Somersby | BEROWRA PA11 | N-1 | 2025 | 350 | 86 | 32 | 32 | 32 | Existing | Project in delivery | 86
Cowan | BEROWRA PA21 | N-1 | 2025 | 350 | 189 | 104 | 104 | 104 | Existing | Under investigation | 189
Blakehurst | BLAKEHURST PA1 | N-1 | 2025 | 355 | 186 | 156 | 156 | 156 | Existing | Under investigation | 186
Blakehurst | BLAKEHURST PA12 | N-1 | 2025 | 355 | 179 | 90 | 90 | 90 | Existing | Under investigation | 179
Branxton | BRANXTON 66 PA13 | N-1 | 2024 | 400 | 232 | 85 | 85 | 85 | Existing | Project under development | 232
Burwood | BURWOOD PA09 | N-1 | 2025 | 390 | 266 | 53 | 53 | 53 | Existing | Under investigation | 266
Canada Bay | BURWOOD PA19 | N-1 | 2025 | 400 | 158 | 136 | 136 | 136 | Existing | Under investigation | 158
Cardiff | CARDIFF 33 PA01 | N-1 | 2025 | 301 | 236 | 46 | 46 | 46 | Existing | Under investigation | 236
Warners Bay | CARDIFF 33 PA12 | N-1 | 2025 | 301 | 208 | 22 | 22 | 22 | Existing | Under investigation | 208
Cardiff | CARDIFF 33 PA16 | N-1 | 2025 | 301 | 245 | 80 | 80 | 80 | Existing | Under investigation | 245
Cessnock | CESSNOCK SOUTH PA02 | N-1 | 2024 | 335 | 275 | 180 | 180 | 180 | Existing | Under investigation | 275
Cessnock | CESSNOCK SOUTH PA07 | N-1 | 2025 | 305 | 203 | 60 | 60 | 60 | Existing | Under investigation | 203
Charlestown | CHARLESTOWN 132 PA08 | N-1 | 2025 | 400 | 384 | 119 | 119 | 119 | Existing | Under investigation | 384
Woongarrah | CHARMHAVEN PA01 | N-1 | 2024 | 355 |  | 38 | 38 | 38 | Existing | Project in delivery | 0
Hamlyn Terrace | CHARMHAVEN PA09 | N-1 | 2025 | 305 |  | 104 | 104 | 104 | Existing | Project under development | 0
Woongarrah | CHARMHAVEN PA10 | N-1 | 2025 | 315 |  | 66 | 66 | 66 | Existing | Project under development | 0
Woongarrah | CHARMHAVEN PA12 | N-1 | 2025 | 370 |  | 120 | 120 | 120 | Existing | Project in delivery | 0
Lane Cove | CHATSWOOD PA37 | N-1 | 2025 | 320 | 164 | 194 | 194 | 194 | Existing | Project under development | 164
Lane Cove | CHATSWOOD PA40 | N-1 | 2025 | 400 | 335 | 110 | 110 | 110 | Existing | Project under development | 335
Breakfast Point | CONCORD PA04 | N-1 | 2024 | 320 | 203 | 119 | 119 | 119 | Existing | Project in delivery | 203
Breakfast Point | CONCORD PA17 | N-1 | 2024 | 305 | 180 | 165 | 165 | 165 | Existing | Project in delivery | 180
Breakfast Point | CONCORD PA18 | N-1 | 2024 | 315 | 185 | 79 | 79 | 79 | Existing | Project in delivery | 185
Breakfast Point | CONCORD PA22 | N-1 | 2024 | 315 | 177 | 135 | 135 | 135 | Existing | Project in delivery | 177
Warners Bay | CROUDANCE BAY PA01 | N-1 | 2025 | 282 | 284 | 196 | 196 | 196 | Existing | Under investigation | 284
Valentine | CROUDANCE BAY PA02 | N-1 | 2025 | 373 | 114 | 69 | 69 | 69 | Existing | Under investigation | 114
Belmont | CROUDANCE BAY PA06 | N-1 | 2025 | 373 | 260 | 104 | 104 | 104 | Existing | Under investigation | 260
Valentine | CROUDANCE BAY PA12 | N-1 | 2025 | 337 | 279 | 206 | 206 | 206 | Existing | Under investigation | 279
Pyrmont | DARLING HARBOUR 132/11kV PA09 | N-1 | 2025 | 400 | 287 | 40 | 40 | 40 | Existing | Project in delivery | 287
Cameron Park | EDGEWORTH 33 PA01 | N-1 | 2024 | 293 | 293 | 51 | 51 | 51 | Existing | Under investigation | 293
Cameron Park | EDGEWORTH 33 PA07 | N-1 | 2025 | 258 | 216 | 41 | 41 | 41 | Existing | Under investigation | 216
Cameron Park | EDGEWORTH 33 PA09 | N-1 | 2024 | 263 | 197 | 100 | 100 | 100 | Existing | Under investigation | 197
Holmesville | EDGEWORTH 33 PA10 | N-1 | 2024 | 400 | 359 | 108 | 108 | 108 | Existing | Under investigation | 359
Kilcare | EMPIRE BAY PA08 | N-1 | 2024 | 400 | 176 | 87 | 87 | 87 | Existing | Under investigation | 176
Green Point | ERINA PA01 | N-1 | 2025 | 400 | 195 | 33 | 33 | 33 | Existing | Under investigation | 195
Erina | ERINA PA07 | N-1 | 2025 | 400 | 266 | 123 | 123 | 123 | Existing | Under investigation | 266
Erina | ERINA PA13 | N-1 | 2025 | 280 |  | 35 | 35 | 35 | Existing | Under investigation | 0
Homebush | FLEMINGTON PA04 | N-1 | 2025 | 300 | 185 | 175 | 175 | 175 | Existing | Project under development | 185
Putney | HUNTERS HILL PA36 | N-1 | 2025 | 340 | 158 | 50 | 50 | 50 | Existing | Under investigation | 158
Riverview | HUNTERS HILL PA41 | N-1 | 2025 | 330 | 155 | 47 | 47 | 47 | Existing | Under investigation | 155
Riverview | HUNTERS HILL PA57 | N-1 | 2025 | 315 | 159 | 38 | 38 | 38 | Existing | Under investigation | 159
Woronora | JANNALI PA25 | N-1 | 2025 | 315 | 121 | 150 | 150 | 150 | Existing | Under investigation | 121
Kurri Kurri | KURRI 132/11kV PA06 | N-1 | 2024 | 400 | 242 | 162 | 162 | 162 | Existing | Under investigation | 242
Heddon Greta | KURRI 132/11kV PA12 | N-1 | 2025 | 400 | 306 | 50 | 50 | 50 | Existing | Under investigation | 306
Gillieston Heights | KURRI 132/11kV PA19 | N-1 | 2024 | 400 | 329 | 115 | 115 | 115 | Existing | Under investigation | 329
Summerland Point | LAKE MUNMORAH PA07 | N-1 | 2024 | 390 | 382 | 152.3997 | 152 | 152 | Existing | Under investigation | 382
Bateau Bay | LONG JETTY PA02 | N-1 | 2024 | 280 | 176 | 145 | 145 | 145 | Existing | Under investigation | 176
Maitland Vale | MAITLAND 33 PA04 | N & N-1 | 2024 | 270 | 222 | 240 | 240 | 240 | Existing | Project under development | 222
Aberglasslyn | MAITLAND 33 PA07 | N & N-1 | 2024 | 290 | 310 | 249 | 249 | 249 | Existing | Project under development | 310
Largs | MAITLAND 33 PA11 | N & N-1 | 2024 | 260 | 257 | 133 | 133 | 133 | Existing | Project under development | 257
Bolwarra Heights | MAITLAND 33 PA13 | N-1 | 2024 | 260 | 226 | 193 | 193 | 193 | Existing | Project under development | 226
Fletcher | MARYLAND 132 PA02 | N-1 | 2024 | 384 | 238 | 67 | 67 | 67 | Existing | Under investigation | 238
Fletcher | MARYLAND 132 PA06 | N-1 | 2024 | 384 | 290 | 53 | 53 | 53 | Existing | Under investigation | 290
Cameron Park | MARYLAND 132 PA10 | N-1 | 2024 | 400 | 102 | 26 | 26 | 26 | Existing | Under investigation | 102
Muswellbrook | MITCHELL LINE 66 PA11 | N-1 | 2024 | 400 | 199 | 100 | 100 | 100 | Existing | Project under development | 199
Wyee | MORISSET 132 PA06 | N-1 | 2024 | 364 | 251 | 64 | 64 | 64 | Existing | Project under development | 251
Mosman | MOSMAN PA36 | N-1 | 2025 | 350 | 112 | 26 | 26 | 26 | Existing | Under investigation | 112
Eleebana | MT HUTTON PA03 | N-1 | 2025 | 288 | 255 | 53 | 53 | 53 | Existing | Under investigation | 255
Anna Bay | NELSON BAY 33 PA03 | N-1 | 2025 | 398 | 163 | 31 | 31 | 31 | Existing | Under investigation | 163
Soldiers Point | NELSON BAY 33 PA04 | N-1 | 2024 | 282 | 232 | 109 | 109 | 109 | Existing | Under investigation | 232
Nelson Bay | NELSON BAY 33 PA05 | N-1 | 2025 | 263 | 211 | 124 | 124 | 124 | Existing | Under investigation | 211
Anna Bay | NELSON BAY 33 PA09 | N-1 | 2025 | 385 | 147 | 183 | 183 | 183 | Existing | Under investigation | 147
Bar Beach | NEWCASTLE CBD 33 PA30 | N-1 | 2024 | 265 | 241 | 26 | 26 | 26 | Existing | Under investigation | 241
Cessnock | NULKABA 33 PA05 | N-1 | 2025 | 400 | 277 | 93 | 93 | 93 | Existing | Under investigation | 277
Homebush | OLYMPIC PARK PA06 | N-1 | 2025 | 400 | 184 | 88 | 88 | 88 | Existing | Project under development | 184
Homebush | OLYMPIC PARK PA10 | N-1 | 2025 | 400 | 108 | 121 | 121 | 121 | Existing | Project under development | 108
Blacksmiths | PELICAN 33 PA01 | N-1 | 2025 | 400 | 178 | 46 | 46 | 46 | Existing | Under investigation | 178
Rathmines | RATHMINES 132 PA10 | N-1 | 2024 | 288 | 197 | 180 | 180 | 180 | Existing | Under investigation | 197
Raymond Terrace | RAYMOND TERRACE 33 PA04 | N-1 | 2025 | 308 | 51 | 20 | 20 | 20 | Existing | Under investigation | 51
Rose Bay | ROSE BAY PA13 | N-1 | 2025 | 290 | 195 | 78 | 78 | 78 | Existing | Under investigation | 195
Aberglasslyn | RUTHERFORD 33 PA02 | N & N-1 | 2024 | 350 | 366 | 396 | 396 | 396 | Existing | Project under development | 366
Rutherford | RUTHERFORD 33 PA03 | N-1 | 2024 | 380 | 281 | 36 | 36 | 36 | Existing | Project under development | 281
Rutherford | RUTHERFORD 33 PA09 | N-1 | 2024 | 350 | 161 | 151 | 151 | 151 | Existing | Project under development | 161
Whittingham / Abattoir | SINGLETON 66 PA28 | N-1 | 2024 | 400 | 244 | 145 | 145 | 145 | Existing | Under investigation | 244
Kariong | SOMERSBY PA16 | N-1 | 2025 | 295 | 219 | 32 | 32 | 32 | Existing | Under investigation | 219
Somersby | SOMERSBY PA17 | N-1 | 2024 | 295 | 85 | 63 | 63 | 63 | Existing | Under investigation | 85
Redfern | ST. PETERS PA20 | N-1 | 2025 | 400 | 212 | 28 | 28 | 28 | Existing | Under investigation | 212
Erskineville | ST. PETERS PA32 | N-1 | 2025 | 316 | 197 | 45 | 45 | 45 | Existing | Under investigation | 197
Tanilba Bay | TANILBA BAY 33 PA15 | N-1 | 2025 | 337 | 151 | 200 | 200 | 200 | Existing | Under investigation | 151
Rutherford | TELARAH 33 PA08 | N-1 | 2024 | 295 | 247 | 156 | 156 | 156 | Existing | Project under development | 247
Rutherford | TELARAH 33 PA10 | N-1 | 2024 | 295 | 203 | 64 | 64 | 64 | Existing | Project under development | 203
Chisholm | THORNTON 33 PA04 | N-1 | 2025 | 383 | 174 | 88 | 88 | 88 | Existing | Project in delivery | 174
Thornton | THORNTON 33 PA11 | N-1 | 2024 | 310 | 223 | 145 | 145 | 190 | Existing | Project in delivery | 223
Thornton | THORNTON 33 PA18 | N-1 | 2024 | 290 | 318 | 196 | 196 | 196 | Existing | Project under development | 318
Chisholm | THORNTON 33 PA20 | N-1 | 2025 | 380 | 252 | 108 | 108 | 348 | Existing | Project in delivery | 252
Tighes Hill / Islington | TIGHES HILL PA09 | N-1 | 2025 | 400 | 144 | 47 | 47 | 47 | 2026 | Project under development | 144
Broadmeadow | TIGHES HILL PA17 | N-1 | 2025 | 400 | 216 | 38 | 38 | 38 | Existing | Project under development | 216
Nelson Bay | TOMAREE 33 PA13 | N-1 | 2025 | 400 | 217 | 75 | 75 | 75 | Existing | Under investigation | 217
Coal Point | TORONTO WEST 132 PA08 | N-1 | 2025 | 335 | 203 | 24 | 24 | 24 | Existing | Under investigation | 203
Gosford | WEST GOSFORD PA03 | N-1 | 2025 | 365 | 164 | 272 | 272 | 272 | Existing | Under investigation | 164
Gosford | WEST GOSFORD PA12 | N-1 | 2025 | 400 | 305 | 28 | 28 | 28 | Existing | Under investigation | 305
Williamtown | WILLIAMTOWN PA01 | N-1 | 2025 | 224 | 122 | 246 | 246 | 246 | Existing | Project in delivery | 122
Fern Bay | WILLIAMTOWN PA02 | N-1 | 2025 | 148 | 13 | 103 | 103 | 103 | Existing | Under investigation | 13
Williamtown | WILLIAMTOWN PA04 | N-1 | 2025 | 484 | 29 | 269 | 269 | 269 | Existing | Project in delivery | 29
Saratoga | WOY WOY PA06 | N-1 | 2025 | 290 | 58 | 32 | 32 | 32 | Existing | Under investigation | 58
Warnervale | WYONG PA03 | N-1 | 2025 | 285 |  | 167 | 167 | 167 | Existing | Project under development | 0
Jilliby | WYONG PA05 | N-1 | 2024 | 285 | 220 | 76.4993 | 76 | 76 | Existing | Project under development | 220
Tacoma | WYONG PA10 | N-1 | 2024 | 355 | 238 | 216.415 | 216 | 216 | Existing | Project under development | 238
Wyong Creek | WYONG PA12 | N-1 | 2024 | 370 |  | 74.248 | 74 | 74 | Existing | Project under development | 0
Jilliby | WYONG PA14 | N-1 | 2025 | 400 | 183 | 217 | 217 | 217 | Existing | Project under development | 183
Waterloo | ZETLAND PA10 | N-1 | 2025 | 355 | 186 | 26 | 26 | 26 | Existing | Project under development | 186

## SON (hidden)
Feeder L/R | Feeder (Non L/R ) | Double Banked | Area | Zone | 300A Rating Applied | 2025 Trunk Summer Rating | 2025 FY LIS MW | 2025 FY LIS Amps |  | Zone | Panel |  | Panel OMS | Zone | Area Plan | Max LAR All | Max LAR (Capped at 150) | Location | Location | Feeder Name
D.F.ZN00080/00021R | D.F.ZN00080/000021 | 0 | Lower North Shore | CHATSWOOD |  | 315 | 3.4344 | 180.258 |  | ZN00224 | CBZZN00224PA11 | PA11 | 224:80346 | ARGENTON 132/11 | Newcastle Western Corridor | 178.6974 | 150 | Speers Point | Speers Point | ARGENTON 132/11 PA11
D.F.ZN00080/00021L | D.F.ZN00080/000021 | 1 | Lower North Shore | CHATSWOOD |  | 305 | 0.3319 | 17.4224 |  | ZN12570 | CBZZN12570PA24 | PA24 | ZN12570:PA24 | AVOCA | Lower Central Coast | 164 | 150 | MacMasters Beach | Macmasters Beach | AVOCA PA24
D.F.ZN00080/000022 | D.F.ZN00080/000022 | 0 | Lower North Shore | CHATSWOOD |  | 400 | 3.622 | 190.1043 |  | ZN12570 | CBZZN12570PA33 | PA33 | ZN12570:PA33 | AVOCA | Lower Central Coast | 60.6129 | 60.6129 | MacMasters Beach | Macmasters Beach | AVOCA PA33
D.F.ZN00080/00024L | D.F.ZN00080/000024 | 0 | Lower North Shore | CHATSWOOD |  | 330 | 3.4037 | 178.6466 |  | ZN35800 | CBZZN35800PA10 | PA10 | ZN35800:PA10 | BANKSTOWN | Canterbury Bankstown | 50 | 50 | Punchbowl | Punchbowl | BANKSTOWN PA10
D.F.ZN00080/00024R | D.F.ZN00080/000024 | 1 | Lower North Shore | CHATSWOOD |  | 400 | 1.2566 | 65.953
D.F.ZN00080/000025 | D.F.ZN00080/000025 | 0 | Lower North Shore | CHATSWOOD |  | 320 | 2.5596 | 134.3443
D.F.ZN00080/000028 | D.F.ZN00080/000028 | 0 | Lower North Shore | CHATSWOOD |  | 230 | 1.6318 | 85.6487
D.F.ZN00080/00030R | D.F.ZN00080/000030 | 0 | Lower North Shore | CHATSWOOD |  | 390 | 2.3644 | 124.097
D.F.ZN00080/00030L | D.F.ZN00080/000030 | 1 | Lower North Shore | CHATSWOOD |  | 330 | 1.9009 | 99.7721
D.F.ZN00080/000031 | D.F.ZN00080/000031 | 0 | Lower North Shore | CHATSWOOD |  | 330 | 2.9293 | 153.7482
D.F.ZN00080/00032R | D.F.ZN00080/000032 | 0 | Lower North Shore | CHATSWOOD |  | 400 | 3.1899 | 167.4238
D.F.ZN00080/00032L | D.F.ZN00080/000032 | 1 | Lower North Shore | CHATSWOOD |  | 305 | 2.9488 | 154.7733
D.F.ZN00080/000034 | D.F.ZN00080/000034 | 0 | Lower North Shore | CHATSWOOD |  | 330 | 0.9424 | 49.465
D.F.ZN00080/000036 | D.F.ZN00080/000036 | 0 | Lower North Shore | CHATSWOOD |  | 295 | 1.3081 | 68.6579
D.F.ZN00080/00037R | D.F.ZN00080/000037 | 0 | Lower North Shore | CHATSWOOD |  | 305 | 3.2393 | 170.0181
D.F.ZN00080/00037L | D.F.ZN00080/000037 | 1 | Lower North Shore | CHATSWOOD |  | 320 | 3.1256 | 164.0529 | 1
D.F.ZN00080/000039 | D.F.ZN00080/000039 | 0 | Lower North Shore | CHATSWOOD |  | 335 | 1.2451 | 65.3486
D.F.ZN00080/00040R | D.F.ZN00080/000040 | 0 | Lower North Shore | CHATSWOOD |  | 305 | 4.516 | 237.0262 | 1 | 335.0532
D.F.ZN00080/00040L | D.F.ZN00080/000040 | 1 | Lower North Shore | CHATSWOOD |  | 365 | 1.8677 | 98.027 | 1
D.F.ZN00080/000041 | D.F.ZN00080/000041 | 0 | Lower North Shore | CHATSWOOD |  | 340 |  | 0
D.F.ZN00116/000001 | D.F.ZN00116/000001 | 0 | Inner West Sydney | LEICHHARDT |  | 390 | 2.9507 | 154.8726
D.F.ZN00116/00002L | D.F.ZN00116/000002 | 0 | Inner West Sydney | LEICHHARDT |  | 330 | 2.7263 | 143.0921
D.F.ZN00116/000004 | D.F.ZN00116/000004 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 2.7803 | 145.9265
D.F.ZN00116/000007 | D.F.ZN00116/000007 | 0 | Inner West Sydney | LEICHHARDT |  | 390 | 0.1842 | 9.668
D.F.ZN00116/000008 | D.F.ZN00116/000008 | 0 | Inner West Sydney | LEICHHARDT |  | 395 | 0.9553 | 50.1384
D.F.ZN00116/000012 | D.F.ZN00116/000012 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 4.5469 | 238.65
D.F.ZN00116/00014L | D.F.ZN00116/000014 | 0 | Inner West Sydney | LEICHHARDT |  | 330 | 2.0844 | 109.4027
D.F.ZN00116/000015 | D.F.ZN00116/000015 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 4.2466 | 222.8886
D.F.ZN00116/000019 | D.F.ZN00116/000019 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 4.5654 | 239.6223
D.F.ZN00116/000020 | D.F.ZN00116/000020 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 3.3545 | 176.0669
D.F.ZN00116/000023 | D.F.ZN00116/000023 | 0 | Inner West Sydney | LEICHHARDT |  | 370 | 2.1994 | 115.4383
D.F.ZN00116/00025L | D.F.ZN00116/000025 | 0 | Inner West Sydney | LEICHHARDT |  | 245 | 3.2154 | 168.7649
D.F.ZN00116/000026 | D.F.ZN00116/000026 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 1.6654 | 87.4106
D.F.ZN00116/000029 | D.F.ZN00116/000029 | 0 | Inner West Sydney | LEICHHARDT |  | 330 | 1.8586 | 97.5498
D.F.ZN00116/000030 | D.F.ZN00116/000030 | 0 | Inner West Sydney | LEICHHARDT |  | 400 | 2.7038 | 141.9109
D.F.ZN00116/000031 | D.F.ZN00116/000031 | 0 | Inner West Sydney | LEICHHARDT |  | 330 | 3.7966 | 199.2673
D.F.ZN00129/000034 | D.F.ZN00129/000034 | 0 | Carlingford | HUNTERS HILL |  | 320 | 2.0974 | 110.0852
D.F.ZN00129/000035 | D.F.ZN00129/000035 | 0 | Carlingford | HUNTERS HILL |  | 400 | 3.7881 | 198.8215
D.F.ZN00129/000036 | D.F.ZN00129/000036 | 0 | Carlingford | HUNTERS HILL |  | 340 | 3.0069 | 157.8188 | 1
D.F.ZN00129/000038 | D.F.ZN00129/000038 | 0 | Carlingford | HUNTERS HILL |  | 300 | 3.1729 | 166.5365
D.F.ZN00129/000039 | D.F.ZN00129/000039 | 0 | Carlingford | HUNTERS HILL |  | 330 | 1.8899 | 99.1933
D.F.ZN00129/000040 | D.F.ZN00129/000040 | 0 | Carlingford | HUNTERS HILL |  | 380 | 2.7975 | 146.8287
D.F.ZN00129/000041 | D.F.ZN00129/000041 | 0 | Carlingford | HUNTERS HILL |  | 330 | 2.9619 | 155.4602 | 1
D.F.ZN00129/000043 | D.F.ZN00129/000043 | 0 | Carlingford | HUNTERS HILL |  | 340 | 1.7657 | 92.677
D.F.ZN00129/000046 | D.F.ZN00129/000046 | 0 | Carlingford | HUNTERS HILL |  | 300 | 3.2075 | 168.3513
D.F.ZN00129/000047 | D.F.ZN00129/000047 | 0 | Carlingford | HUNTERS HILL |  | 380 | 3.1223 | 163.8772
D.F.ZN00129/000049 | D.F.ZN00129/000049 | 0 | Carlingford | HUNTERS HILL |  | 400 | 1.8707 | 98.1884
D.F.ZN00129/000050 | D.F.ZN00129/000050 | 0 | Carlingford | HUNTERS HILL |  | 315 |  | 0
D.F.ZN00129/000051 | D.F.ZN00129/000051 | 0 | Carlingford | HUNTERS HILL |  | 400 | 3.2069 | 168.3162
D.F.ZN00129/000052 | D.F.ZN00129/000052 | 0 | Carlingford | HUNTERS HILL |  | 400 | 4.2877 | 225.0433
D.F.ZN00129/000055 | D.F.ZN00129/000055 | 0 | Carlingford | HUNTERS HILL |  | 340 | 1.0539 | 55.318
D.F.ZN00129/000056 | D.F.ZN00129/000056 | 0 | Carlingford | HUNTERS HILL |  | 400 | 4.834 | 253.7217
D.F.ZN00129/000057 | D.F.ZN00129/000057 | 0 | Carlingford | HUNTERS HILL |  | 315 | 3.0303 | 159.05 | 1
D.F.ZN00129/000061 | D.F.ZN00129/000061 | 0 | Carlingford | HUNTERS HILL |  | 345 |  | 0
D.F.ZN00129/000062 | D.F.ZN00129/000062 | 0 | Carlingford | HUNTERS HILL |  | 330 | 0.9977 | 52.3667
D.F.ZN00129/000063 | D.F.ZN00129/000063 | 0 | Carlingford | HUNTERS HILL |  | 400 | 4.0987 | 215.1278
D.F.ZN00129/000064 | D.F.ZN00129/000064 | 0 | Carlingford | HUNTERS HILL |  | 400 | 4.5374 | 238.154
D.F.ZN00167/00001L | D.F.ZN00167/000001 | 0 | Inner West Sydney | AUBURN |  | 225 | 1.692 | 88.8068
D.F.ZN00167/000002 | D.F.ZN00167/000002 | 0 | Inner West Sydney | AUBURN |  | 300 | 3.0727 | 161.2736
D.F.ZN00167/000004 | D.F.ZN00167/000004 | 0 | Inner West Sydney | AUBURN |  | 335 | 1.194 | 62.6682
D.F.ZN00167/000007 | D.F.ZN00167/000007 | 0 | Inner West Sydney | AUBURN |  | 315 | 2.3579 | 123.7579
D.F.ZN00167/000008 | D.F.ZN00167/000008 | 0 | Inner West Sydney | AUBURN |  | 400 | 1.7665 | 92.7185
D.F.ZN00167/000010 | D.F.ZN00167/000010 | 0 | Inner West Sydney | AUBURN |  | 400 | 2.981 | 156.463
D.F.ZN00167/000011 | D.F.ZN00167/000011 | 0 | Inner West Sydney | AUBURN |  | 315 | 1.5008 | 78.7719
D.F.ZN00167/000012 | D.F.ZN00167/000012 | 0 | Inner West Sydney | AUBURN |  | 315 | 2.3622 | 123.9848
D.F.ZN00167/000013 | D.F.ZN00167/000013 | 0 | Inner West Sydney | AUBURN |  | 400 | 2.0392 | 107.0301
D.F.ZN00167/000014 | D.F.ZN00167/000014 | 0 | Inner West Sydney | AUBURN |  | 300 | 1.7042 | 89.448
D.F.ZN00167/000015 | D.F.ZN00167/000015 | 0 | Inner West Sydney | AUBURN |  | 400 | 1.7696 | 92.8775
D.F.ZN00167/000017 | D.F.ZN00167/000017 | 0 | Inner West Sydney | AUBURN |  | 315 | 2.9507 | 154.8691
D.F.ZN00167/000019 | D.F.ZN00167/000019 | 0 | Inner West Sydney | AUBURN |  | 340 | 2.7406 | 143.8449
D.F.ZN00167/00020L | D.F.ZN00167/000020 | 0 | Inner West Sydney | AUBURN |  | 380 | 2.3687 | 124.3243
D.F.ZN00167/000021 | D.F.ZN00167/000021 | 0 | Inner West Sydney | AUBURN |  | 400 | 2.22 | 116.519
D.F.ZN00180/00007L | D.F.ZN00180/000007 | 0 | Lower North Shore | MOSMAN |  | 345 | 2.9727 | 156.0273
D.F.ZN00180/000009 | D.F.ZN00180/000009 | 0 | Lower North Shore | MOSMAN |  | 295 | 1.8428 | 96.7217
D.F.ZN00180/000010 | D.F.ZN00180/000010 | 0 | Lower North Shore | MOSMAN |  | 295 | 2.8743 | 150.8637
D.F.ZN00180/000015 | D.F.ZN00180/000015 | 0 | Lower North Shore | MOSMAN |  | 295 | 2.5334 | 132.9684
D.F.ZN00180/000016 | D.F.ZN00180/000016 | 0 | Lower North Shore | MOSMAN |  | 295 | 1.4354 | 75.3394
D.F.ZN00180/000017 | D.F.ZN00180/000017 | 0 | Lower North Shore | MOSMAN |  | 290 | 2.294 | 120.4029
D.F.ZN00180/000018 | D.F.ZN00180/000018 | 0 | Lower North Shore | MOSMAN |  | 310 | 1.4641 | 76.8461
D.F.ZN00180/000019 | D.F.ZN00180/000019 | 0 | Lower North Shore | MOSMAN |  | 400 | 3.0388 | 159.4962
D.F.ZN00180/000020 | D.F.ZN00180/000020 | 0 | Lower North Shore | MOSMAN |  | 400 | 2.1884 | 114.8629
D.F.ZN00180/000021 | D.F.ZN00180/000021 | 0 | Lower North Shore | MOSMAN |  | 400 | 2.8534 | 149.7641
D.F.ZN00180/000022 | D.F.ZN00180/000022 | 0 | Lower North Shore | MOSMAN |  | 290 | 4.4882 | 235.568
D.F.ZN00180/000023 | D.F.ZN00180/000023 | 0 | Lower North Shore | MOSMAN |  | 400 | 2.9134 | 152.9114
D.F.ZN00180/000024 | D.F.ZN00180/000024 | 0 | Lower North Shore | MOSMAN |  | 300 | 2.9526 | 154.9712
D.F.ZN00180/000027 | D.F.ZN00180/000027 | 0 | Lower North Shore | MOSMAN |  | 305 | 1.8173 | 95.3814
D.F.ZN00180/00028L | D.F.ZN00180/000028 | 0 | Lower North Shore | MOSMAN |  | 215 | 2.0754 | 108.9305
D.F.ZN00180/000029 | D.F.ZN00180/000029 | 0 | Lower North Shore | MOSMAN |  | 305 | 2.2463 | 117.9016
D.F.ZN00180/00030L | D.F.ZN00180/000030 | 0 | Lower North Shore | MOSMAN |  | 280 | 2.3501 | 123.3505
D.F.ZN00180/000031 | D.F.ZN00180/000031 | 0 | Lower North Shore | MOSMAN |  | 290 | 3.0933 | 162.3581
D.F.ZN00180/00032L | D.F.ZN00180/000032 | 0 | Lower North Shore | MOSMAN |  | 370 | 2.3321 | 122.4028
D.F.ZN00180/000033 | D.F.ZN00180/000033 | 0 | Lower North Shore | MOSMAN |  | 295 | 3.9376 | 206.6695
D.F.ZN00180/000034 | D.F.ZN00180/000034 | 0 | Lower North Shore | MOSMAN |  | 315 | 1.6754 | 87.9359
D.F.ZN00180/000035 | D.F.ZN00180/000035 | 0 | Lower North Shore | MOSMAN |  | 180 | 4.8778 | 256.0155
D.F.ZN00180/000036 | D.F.ZN00180/000036 | 0 | Lower North Shore | MOSMAN |  | 350 | 2.1374 | 112.1854
D.F.ZN00180/000041 | D.F.ZN00180/000041 | 0 | Lower North Shore | MOSMAN |  | 315 | 4.6978 | 246.5688
D.F.ZN00180/000042 | D.F.ZN00180/000042 | 0 | Lower North Shore | MOSMAN |  | 290 | 3.3417 | 175.3937
D.F.ZN00180/000043 | D.F.ZN00180/000043 | 0 | Lower North Shore | MOSMAN |  | 315 | 3.6467 | 191.4031
D.F.ZN00180/000044 | D.F.ZN00180/000044 | 0 | Lower North Shore | MOSMAN |  | 350 | 1.2269 | 64.3951
D.F.ZN00187/00004R | D.F.ZN00187/000004 | 0 | Lower North Shore | CROWS NEST |  | 400 | 3.0736 | 161.324
D.F.ZN00187/000006 | D.F.ZN00187/000006 | 0 | Lower North Shore | CROWS NEST |  | 400 | 2.0359 | 106.8573
D.F.ZN00187/00007L | D.F.ZN00187/000007 | 0 | Lower North Shore | CROWS NEST |  | 400 | 1.6591 | 87.0819
D.F.ZN00187/00008L | D.F.ZN00187/000008 | 0 | Lower North Shore | CROWS NEST |  | 400 | 2.1999 | 115.4672
D.F.ZN00187/000010 | D.F.ZN00187/000010 | 0 | Lower North Shore | CROWS NEST |  | 230 | 1.0136 | 53.1987
D.F.ZN00187/00012L | D.F.ZN00187/000012 | 0 | Lower North Shore | CROWS NEST |  | 390 | 1.8903 | 99.2142
D.F.ZN00187/00013L | D.F.ZN00187/000013 | 0 | Lower North Shore | CROWS NEST |  | 230 | 3.0336 | 159.2234
D.F.ZN00187/00014L | D.F.ZN00187/000014 | 0 | Lower North Shore | CROWS NEST |  | 400 | 1.9223 | 100.8956
D.F.ZN00187/00016L | D.F.ZN00187/000016 | 0 | Lower North Shore | CROWS NEST |  | 275 | 2.4029 | 126.1214
D.F.ZN00187/000017 | D.F.ZN00187/000017 | 0 | Lower North Shore | CROWS NEST |  | 400 | 2.7776 | 145.7841
D.F.ZN00187/000019 | D.F.ZN00187/000019 | 0 | Lower North Shore | CROWS NEST |  | 305 | 1.2623 | 66.253
D.F.ZN00187/000020 | D.F.ZN00187/000020 | 0 | Lower North Shore | CROWS NEST |  | 400 | 2.1983 | 115.382
D.F.ZN00187/000021 | D.F.ZN00187/000021 | 0 | Lower North Shore | CROWS NEST |  | 400 | 2.7876 | 146.3097
D.F.ZN00187/000022 | D.F.ZN00187/000022 | 0 | Lower North Shore | CROWS NEST |  | 400 | 1.6776 | 88.0524
D.F.ZN00187/00023L | D.F.ZN00187/000023 | 0 | Lower North Shore | CROWS NEST |  | 310 | 1.4494 | 76.074
D.F.ZN00187/00023R | D.F.ZN00187/000023 | 1 | Lower North Shore | CROWS NEST |  | 400 | 1.6149 | 84.761
D.F.ZN00187/000024 | D.F.ZN00187/000024 | 0 | Lower North Shore | CROWS NEST |  | 400 | 1.3589 | 71.3222
D.F.ZN00187/000026 | D.F.ZN00187/000026 | 0 | Lower North Shore | CROWS NEST |  | 250 | 0.6902 | 36.2251
D.F.ZN00187/000028 | D.F.ZN00187/000028 | 0 | Lower North Shore | CROWS NEST |  | 400 | 2.8994 | 152.1815
D.F.ZN00187/00029L | D.F.ZN00187/000029 | 0 | Lower North Shore | CROWS NEST |  | 220 | 1.5132 | 79.4243
D.F.ZN00187/00029R | D.F.ZN00187/000029 | 1 | Lower North Shore | CROWS NEST |  | 400 | 1.4241 | 74.744
D.F.ZN00187/00030L | D.F.ZN00187/000030 | 0 | Lower North Shore | CROWS NEST |  | 400 | 3.6489 | 191.5169
D.F.ZN00187/00030R | D.F.ZN00187/000030 | 1 | Lower North Shore | CROWS NEST |  | 400 |  | 0
D.F.ZN00188/000001 | D.F.ZN00188/000001 | 0 | Eastern Suburbs Inner | ZETLAND |  | 355 | 1.638 | 85.9731
D.F.ZN00188/000002 | D.F.ZN00188/000002 | 0 | Eastern Suburbs Inner | ZETLAND |  | 400 | 1.8403 | 96.5926
D.F.ZN00188/000003 | D.F.ZN00188/000003 | 0 | Eastern Suburbs Inner | ZETLAND |  | 380 | 1.7452 | 91.6015
D.F.ZN00188/000004 | D.F.ZN00188/000004 | 0 | Eastern Suburbs Inner | ZETLAND |  | 285 | 1.2997 | 68.2151
D.F.ZN00188/00005L | D.F.ZN00188/000005 | 0 | Eastern Suburbs Inner | ZETLAND |  | 275 | 1.0817 | 56.7736
D.F.ZN00188/000006 | D.F.ZN00188/000006 | 0 | Eastern Suburbs Inner | ZETLAND |  | 295 | 0.674 | 35.3751
D.F.ZN00188/000009 | D.F.ZN00188/000009 | 0 | Eastern Suburbs Inner | ZETLAND |  | 265 | 2.6366 | 138.3853
D.F.ZN00188/00010L | D.F.ZN00188/000010 | 0 | Eastern Suburbs Inner | ZETLAND |  | 355 | 3.5364 | 185.613 | 1
D.F.ZN00188/00013R | D.F.ZN00188/000013 | 0 | Eastern Suburbs Inner | ZETLAND |  | 330 | 1.436 | 75.3728
D.F.ZN00188/00013L | D.F.ZN00188/000013 | 1 | Eastern Suburbs Inner | ZETLAND |  | 295 | 1.2306 | 64.5903
D.F.ZN00188/000014 | D.F.ZN00188/000014 | 0 | Eastern Suburbs Inner | ZETLAND |  | 385 | 0.6682 | 35.0699
D.F.ZN00188/000015 | D.F.ZN00188/000015 | 0 | Eastern Suburbs Inner | ZETLAND |  | 255 | 1.6273 | 85.4121
D.F.ZN00188/000016 | D.F.ZN00188/000016 | 0 | Eastern Suburbs Inner | ZETLAND |  | 270 | 2.4306 | 127.5734
D.F.ZN00188/000017 | D.F.ZN00188/000017 | 0 | Eastern Suburbs Inner | ZETLAND |  | 385 | 4.2867 | 224.9908
D.F.ZN00188/000018 | D.F.ZN00188/000018 | 0 | Eastern Suburbs Inner | ZETLAND |  | 270 | 0.4349 | 22.8278
D.F.ZN00188/000019 | D.F.ZN00188/000019 | 0 | Eastern Suburbs Inner | ZETLAND |  | 345 | 1.2128 | 63.6555
D.F.ZN00188/000020 | D.F.ZN00188/000020 | 0 | Eastern Suburbs Inner | ZETLAND |  | 271 | 0.8317 | 43.6511
D.F.ZN00188/000021 | D.F.ZN00188/000021 | 0 | Eastern Suburbs Inner | ZETLAND |  | 310 | 5.265 | 276.3397
D.F.ZN00188/000022 | D.F.ZN00188/000022 | 0 | Eastern Suburbs Inner | ZETLAND |  | 355 | 3.6861 | 193.4718
D.F.ZN00188/000025 | D.F.ZN00188/000025 | 0 | Eastern Suburbs Inner | ZETLAND |  | 380 | 0.8969 | 47.074
D.F.ZN00188/00026L | D.F.ZN00188/000026 | 0 | Eastern Suburbs Inner | ZETLAND |  | 355 | 3.4206 | 179.5333
D.F.ZN00188/00027L | D.F.ZN00188/000027 | 0 | Eastern Suburbs Inner | ZETLAND |  | 350 | 3.4482 | 180.9834
D.F.ZN00188/000028 | D.F.ZN00188/000028 | 0 | Eastern Suburbs Inner | ZETLAND |  | 305 | 1.5168 | 79.609
D.F.ZN00188/000029 | D.F.ZN00188/000029 | 0 | Eastern Suburbs Inner | ZETLAND |  | 325 | 3.4004 | 178.4767
D.F.ZN00188/000030 | D.F.ZN00188/000030 | 0 | Eastern Suburbs Inner | ZETLAND |  | 370 | 0.6825 | 35.8222
D.F.ZN00188/000031 | D.F.ZN00188/000031 | 0 | Eastern Suburbs Inner | ZETLAND |  | 255 | 4.648 | 243.9568
D.F.ZN00188/000033 | D.F.ZN00188/000033 | 0 | Eastern Suburbs Inner | ZETLAND |  | 385 | 1.8446 | 96.8143
D.F.ZN00188/000034 | D.F.ZN00188/000034 | 0 | Eastern Suburbs Inner | ZETLAND |  | 370 | 0.205 | 10.7577
D.F.ZN00188/000037 | D.F.ZN00188/000037 | 0 | Eastern Suburbs Inner | ZETLAND |  | 255 | 2.069 | 108.5956
D.F.ZN00188/000038 | D.F.ZN00188/000038 | 0 | Eastern Suburbs Inner | ZETLAND |  | 370 | 1.5261 | 80.0983
D.F.ZN00188/00041L | D.F.ZN00188/000041 | 0 | Eastern Suburbs Inner | ZETLAND |  | 370 | 3.9433 | 206.9686
D.F.ZN00188/000042 | D.F.ZN00188/000042 | 0 | Eastern Suburbs Inner | ZETLAND |  | 400 | 2.0694 | 108.6147
D.F.ZN00188/000043 | D.F.ZN00188/000043 | 0 | Eastern Suburbs Inner | ZETLAND |  | 245 | 3.4104 | 179.0015
D.F.ZN00188/000044 | D.F.ZN00188/000044 | 0 | Eastern Suburbs Inner | ZETLAND |  | 265 | 2.499 | 131.1613
D.F.ZN00188/000045 | D.F.ZN00188/000045 | 0 | Eastern Suburbs Inner | ZETLAND |  | 340 | 1.7767 | 93.25
D.F.ZN00188/000046 | D.F.ZN00188/000046 | 0 | Eastern Suburbs Inner | ZETLAND |  | 295 | 0.848 | 44.5085
D.F.ZN00195/000003 | D.F.ZN00195/000003 | 0 | Upper North Shore | PYMBLE |  | 380 | 1.7693 | 92.8631
D.F.ZN00195/000004 | D.F.ZN00195/000004 | 0 | Upper North Shore | PYMBLE |  | 400 | 2.0217 | 106.112
D.F.ZN00195/000008 | D.F.ZN00195/000008 | 0 | Upper North Shore | PYMBLE |  | 395 | 1.1507 | 60.3986
D.F.ZN00195/000009 | D.F.ZN00195/000009 | 0 | Upper North Shore | PYMBLE |  | 380 | 4.0298 | 211.5103
D.F.ZN00195/000010 | D.F.ZN00195/000010 | 0 | Upper North Shore | PYMBLE |  | 400 | 2.1838 | 114.6201
D.F.ZN00195/000011 | D.F.ZN00195/000011 | 0 | Upper North Shore | PYMBLE |  | 310 | 2.0491 | 107.5501
D.F.ZN00195/000022 | D.F.ZN00195/000022 | 0 | Upper North Shore | PYMBLE |  | 400 | 1.319 | 69.2312
D.F.ZN00195/000023 | D.F.ZN00195/000023 | 0 | Upper North Shore | PYMBLE |  | 335 | 2.1829 | 114.571
D.F.ZN00195/000025 | D.F.ZN00195/000025 | 0 | Upper North Shore | PYMBLE |  | 305 | 2.8583 | 150.0211
D.F.ZN00195/000028 | D.F.ZN00195/000028 | 0 | Upper North Shore | PYMBLE |  | 400 | 3.1821 | 167.0187
D.F.ZN00195/000029 | D.F.ZN00195/000029 | 0 | Upper North Shore | PYMBLE |  | 305 | 3.367 | 176.7236
D.F.ZN00195/000030 | D.F.ZN00195/000030 | 0 | Upper North Shore | PYMBLE |  | 305 | 3.1663 | 166.1861
D.F.ZN00202/34231R | D.F.ZN00202/034231 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 285 | 0.3957 | 20.771
D.F.ZN00202/034232 | D.F.ZN00202/034232 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 2.4764 | 129.9775
D.F.ZN00202/034234 | D.F.ZN00202/034234 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 223 | 2.0976 | 110.0933
D.F.ZN00202/34237R | D.F.ZN00202/034237 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 285 | 0.3198 | 16.7864
D.F.ZN00202/34237L | D.F.ZN00202/034237 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 285 |  | 0
D.F.ZN00202/34238R | D.F.ZN00202/034238 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 0.2812 | 14.7588
D.F.ZN00202/34238L | D.F.ZN00202/034238 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 0.2482 | 13.0263
D.F.ZN00202/034239 | D.F.ZN00202/034239 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 223 | 0.4985 | 26.165
D.F.ZN00202/34240L | D.F.ZN00202/034240 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 400 | 4.2239 | 221.6983
D.F.ZN00202/34242R | D.F.ZN00202/034242 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 285 | 0.9968 | 52.3169
D.F.ZN00202/34242L | D.F.ZN00202/034242 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 285 | 0.4715 | 24.7461
D.F.ZN00202/34243L | D.F.ZN00202/034243 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 1.0907 | 57.247
D.F.ZN00202/34243R | D.F.ZN00202/034243 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 0.0856 | 4.4907
D.F.ZN00202/034245 | D.F.ZN00202/034245 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 4.5032 | 236.3589
D.F.ZN00202/34246L | D.F.ZN00202/034246 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 400 | 2.815 | 147.7467
D.F.ZN00202/34248L | D.F.ZN00202/034248 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 0.8208 | 43.0796
D.F.ZN00202/34248R | D.F.ZN00202/034248 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 265 |  | 0
D.F.ZN00202/034249 | D.F.ZN00202/034249 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 4.5204 | 237.2583
D.F.ZN00202/034250 | D.F.ZN00202/034250 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 3.6494 | 191.5463
D.F.ZN00202/34253L | D.F.ZN00202/034253 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 2.9109 | 152.7837
D.F.ZN00202/34253R | D.F.ZN00202/034253 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 333 | 0.9161 | 48.0847
D.F.ZN00202/34254R | D.F.ZN00202/034254 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 261 | 4.4277 | 232.3961
D.F.ZN00202/34254L | D.F.ZN00202/034254 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 400 | 2.6442 | 138.787
D.F.ZN00202/034256 | D.F.ZN00202/034256 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 400 | 2.1536 | 113.033
D.F.ZN00202/34259L | D.F.ZN00202/034259 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 339 | 1.1012 | 57.7988
D.F.ZN00202/34259R | D.F.ZN00202/034259 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 400 | 1.0575 | 55.5032
D.F.ZN00202/034260 | D.F.ZN00202/034260 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 4.5979 | 241.3275 | 1
D.F.ZN00202/34261L | D.F.ZN00202/034261 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 223 | 1.8293 | 96.0136
D.F.ZN00202/34261R | D.F.ZN00202/034261 | 1 | Newcastle Inner City | NEWCASTLE CBD |  | 265 | 0.6666 | 34.9874
D.F.ZN00202/34262L | D.F.ZN00202/034262 | 0 | Newcastle Inner City | NEWCASTLE CBD |  | 339 | 2.4702 | 129.6531
D.F.ZN00204/082689 | D.F.ZN00204/082689 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 4.1145 | 215.9545 | 1 | CBZZN00204PA17 | 204:82689 | TIGHES HILL
D.F.ZN00204/082691 | D.F.ZN00204/082691 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 2.7527 | 144.4781 | 1 | CBZZN00204PA09 | 204:82691 | TIGHES HILL
D.F.ZN00204/082692 | D.F.ZN00204/082692 | 0 | Newcastle Inner City | TIGHES HILL |  | 375 | 1.402 | 73.5841
D.F.ZN00204/082695R | D.F.ZN00204/082695 | 0 | Newcastle Inner City | TIGHES HILL |  | 375 |  | 0
D.F.ZN00204/082697 | D.F.ZN00204/082697 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 3.3086 | 173.6558
D.F.ZN00204/082699 | D.F.ZN00204/082699 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 2.0265 | 106.3632
D.F.ZN00204/082700 | D.F.ZN00204/082700 | 0 | Newcastle Inner City | TIGHES HILL |  |  |  | 0
D.F.ZN00204/082701 | D.F.ZN00204/082701 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 3.1135 | 163.4176
D.F.ZN00204/082703 | D.F.ZN00204/082703 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 3.7789 | 198.3428
D.F.ZN00204/082705 | D.F.ZN00204/082705 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 2.1579 | 113.2601
D.F.ZN00204/082708 | D.F.ZN00204/082708 | 0 | Newcastle Inner City | TIGHES HILL |  | 301 | 1.6168 | 84.8603
D.F.ZN00204/082710 | D.F.ZN00204/082710 | 0 | Newcastle Inner City | TIGHES HILL |  | 393 | 0.3023 | 15.8655
D.F.ZN00204/082711 | D.F.ZN00204/082711 | 0 | Newcastle Inner City | TIGHES HILL |  | 400 | 17.8263 | 935.6368
D.F.ZN00205/012202 | D.F.ZN00205/012202 | 0 | Newcastle Inner City | KOTARA |  | 293 | 1.5535 | 81.5387
D.F.ZN00205/012203 | D.F.ZN00205/012203 | 0 | Newcastle Inner City | KOTARA |  | 293 | 3.503 | 183.8584
D.F.ZN00205/012204 | D.F.ZN00205/012204 | 0 | Newcastle Inner City | KOTARA |  | 282 | 4.6687 | 245.0426
D.F.ZN00205/012205 | D.F.ZN00205/012205 | 0 | Newcastle Inner City | KOTARA |  | 304 | 3.899 | 204.6453
D.F.ZN00205/012206 | D.F.ZN00205/012206 | 0 | Newcastle Inner City | KOTARA |  | 293 | 2.3341 | 122.5071
D.F.ZN00205/012208 | D.F.ZN00205/012208 | 0 | Newcastle Inner City | KOTARA |  | 293 | 2.0512 | 107.658
D.F.ZN00205/012209 | D.F.ZN00205/012209 | 0 | Newcastle Inner City | KOTARA |  | 293 | 1.5389 | 80.771
D.F.ZN00205/012210 | D.F.ZN00205/012210 | 0 | Newcastle Inner City | KOTARA |  | 304 | 4.5899 | 240.9061
D.F.ZN00205/012213 | D.F.ZN00205/012213 | 0 | Newcastle Inner City | KOTARA |  | 308 | 3.6079 | 189.3643
D.F.ZN00206/034432 | D.F.ZN00206/034432 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 373 | 4.9579 | 260.2222 | 1 | 3
D.F.ZN00206/034434 | D.F.ZN00206/034434 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 337 | 5.3085 | 278.6219 | 1 | 4
D.F.ZN00206/034435 | D.F.ZN00206/034435 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 282 | 0.7254 | 38.0714
D.F.ZN00206/034437 | D.F.ZN00206/034437 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 400 | 0.1344 | 7.0519
D.F.ZN00206/034438 | D.F.ZN00206/034438 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 373 | 2.175 | 114.1554 | 1 | 2
D.F.ZN00206/034440 | D.F.ZN00206/034440 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 400 | 4.8154 | 252.7417
D.F.ZN00206/034441 | D.F.ZN00206/034441 | 0 | North East Lake Macquarie | CROUDACE BAY |  | 282 | 5.417 | 284.3173 | 1 | 1
D.F.ZN00210/083462 | D.F.ZN00210/083462 | 0 | Newcastle Inner City | NEW LAMBTON |  | 400 | 3.0125 | 158.1127
D.F.ZN00210/083465 | D.F.ZN00210/083465 | 0 | Newcastle Inner City | NEW LAMBTON |  | 400 | 4.3019 | 225.7936
D.F.ZN00210/083466 | D.F.ZN00210/083466 | 0 | Newcastle Inner City | NEW LAMBTON |  | 293 | 1.965 | 103.1357
D.F.ZN00210/083469 | D.F.ZN00210/083469 | 0 | Newcastle Inner City | NEW LAMBTON |  | 400 | 3.0137 | 158.1805
D.F.ZN00210/083472 | D.F.ZN00210/083472 | 0 | Newcastle Inner City | NEW LAMBTON |  | 312 | 1.3783 | 72.3426
D.F.ZN00210/083473 | D.F.ZN00210/083473 | 0 | Newcastle Inner City | NEW LAMBTON |  | 293 | 1.9956 | 104.7405
D.F.ZN00210/083474 | D.F.ZN00210/083474 | 0 | Newcastle Inner City | NEW LAMBTON |  | 332 | 2.622 | 137.6207
D.F.ZN00213/033769 | D.F.ZN00213/033769 | 0 | Newcastle Western Corridor | MARYLAND |  | 384 | 5.5312 | 290.3107 | 1 | CBZZN00213PA02 | 213:33773
D.F.ZN00213/033770 | D.F.ZN00213/033770 | 0 | Newcastle Western Corridor | MARYLAND |  | 286 | 2.885 | 151.4221 |  | CBZZN00213PA06 | 213:33769
D.F.ZN00213/033771 | D.F.ZN00213/033771 | 0 | Newcastle Western Corridor | MARYLAND |  | 384 | 4.884 | 256.3429 |  | CBZZN00213PA10 | 213:33777
D.F.ZN00213/033773 | D.F.ZN00213/033773 | 0 | Newcastle Western Corridor | MARYLAND |  | 384 | 4.5259 | 237.5465 | 1
D.F.ZN00213/033774 | D.F.ZN00213/033774 | 0 | Newcastle Western Corridor | MARYLAND |  | 335 | 4.4204 | 232.0126
D.F.ZN00213/033775 | D.F.ZN00213/033775 | 0 | Newcastle Western Corridor | MARYLAND |  | 400 | 4.1386 | 217.2206
D.F.ZN00213/033777 | D.F.ZN00213/033777 | 0 | Newcastle Western Corridor | MARYLAND |  | 400 | 1.9444 | 102.053 | 1
D.F.ZN00213/033778 | D.F.ZN00213/033778 | 0 | Newcastle Western Corridor | MARYLAND |  | 398 | 0.006 | 0.3126
D.F.ZN00214/008665 | D.F.ZN00214/008665 | 0 | Newcastle Western Corridor | CARDIFF |  | 301 | 4.6698 | 245.0984 | 1
D.F.ZN00214/008666 | D.F.ZN00214/008666 | 0 | Newcastle Western Corridor | CARDIFF |  | 301 | 4.5 | 236.1902 | 1
D.F.ZN00214/008667 | D.F.ZN00214/008667 | 0 | Newcastle Western Corridor | CARDIFF |  | 347 | 3.3414 | 175.3805
D.F.ZN00214/008669 | D.F.ZN00214/008669 | 0 | Newcastle Western Corridor | CARDIFF |  | 301 | 3.8151 | 200.242
D.F.ZN00214/008670 | D.F.ZN00214/008670 | 0 | Newcastle Western Corridor | CARDIFF |  | 301 | 3.9608 | 207.8877 | 1
D.F.ZN00214/008671 | D.F.ZN00214/008671 | 0 | Newcastle Western Corridor | CARDIFF |  | 318 | 1.3117 | 68.8458
D.F.ZN00214/008672 | D.F.ZN00214/008672 | 0 | Newcastle Western Corridor | CARDIFF |  | 347 | 0.6333 | 33.2375
D.F.ZN00216/010722 | D.F.ZN00216/010722 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 400 | 6.8427 | 359.1502 |  | CBZZN00216PA09 | PA9 | 216:10729 | EDGEWORTH 33
D.F.ZN00216/010723 | D.F.ZN00216/010723 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 293 | 2.0081 | 105.3971 |  | CBZZN00216PA10 | PA10 | 216:10722 | EDGEWORTH 33
D.F.ZN00216/010724 | D.F.ZN00216/010724 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 293 | 5.5876 | 293.2708 | 1 | CBZZN00216PA01 | PA1 | 216:10724 | EDGEWORTH 33
D.F.ZN00216/010726 | D.F.ZN00216/010726 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 385 | 3.7823 | 198.5216 |  | CBZZN00216PA07 | PA7 | 216:10728 | EDGEWORTH 33
D.F.ZN00216/010727 | D.F.ZN00216/010727 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 293 | 4.0706 | 213.6507
D.F.ZN00216/010728 | D.F.ZN00216/010728 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 258 | 4.106 | 215.511 | 1
D.F.ZN00216/010729 | D.F.ZN00216/010729 | 0 | Newcastle Western Corridor | EDGEWORTH |  | 263 | 3.7593 | 197.3105
D.F.ZN00217/033605 | D.F.ZN00217/033605 | 0 | #N/A | MOUNT HUTTON |  | 293 |  | 0
D.F.ZN00217/033607 | D.F.ZN00217/033607 | 0 | #N/A | MOUNT HUTTON |  | 400 | 0.2086 | 10.9503
D.F.ZN00217/033608 | D.F.ZN00217/033608 | 0 | #N/A | MOUNT HUTTON |  | 293 | 3.1801 | 166.914
D.F.ZN00217/33610L | D.F.ZN00217/033610 | 0 | #N/A | MOUNT HUTTON |  | 400 | 4.7131 | 247.3732
D.F.ZN00217/033611 | D.F.ZN00217/033611 | 0 | #N/A | MOUNT HUTTON |  | 288 | 4.8635 | 255.2651 | 1
D.F.ZN00217/33612R | D.F.ZN00217/033612 | 0 | #N/A | MOUNT HUTTON |  | 293 | 3.1995 | 167.9286
D.F.ZN00220/008687 | D.F.ZN00220/008687 | 0 | North East Lake Macquarie | JEWELLS |  | 295 | 4.1907 | 219.9545
D.F.ZN00220/008688 | D.F.ZN00220/008688 | 0 | North East Lake Macquarie | JEWELLS |  | 400 | 1.4486 | 76.0315
D.F.ZN00220/008689 | D.F.ZN00220/008689 | 0 | North East Lake Macquarie | JEWELLS |  | 295 | 4.3748 | 229.618
D.F.ZN00220/008691 | D.F.ZN00220/008691 | 0 | North East Lake Macquarie | JEWELLS |  | 295 | 4.0532 | 212.7361
D.F.ZN00220/008692 | D.F.ZN00220/008692 | 0 | North East Lake Macquarie | JEWELLS |  | 400 | 3.3699 | 176.8761
D.F.ZN00221/011893 | D.F.ZN00221/011893 | 0 | North East Lake Macquarie | GATESHEAD |  | 364 | 3.0098 | 157.9729
D.F.ZN00221/011894 | D.F.ZN00221/011894 | 0 | North East Lake Macquarie | GATESHEAD |  | 318 | 2.2996 | 120.6973
D.F.ZN00221/011895 | D.F.ZN00221/011895 | 0 | North East Lake Macquarie | GATESHEAD |  | 301 | 2.6712 | 140.2039
D.F.ZN00221/011897 | D.F.ZN00221/011897 | 0 | North East Lake Macquarie | GATESHEAD |  | 301 | 3.546 | 186.1162
D.F.ZN00221/011898 | D.F.ZN00221/011898 | 0 | North East Lake Macquarie | GATESHEAD |  | 301 | 4.1176 | 216.1187
D.F.ZN00221/011899 | D.F.ZN00221/011899 | 0 | North East Lake Macquarie | GATESHEAD |  | 301 | 3.406 | 178.7675
D.F.ZN00221/011900 | D.F.ZN00221/011900 | 0 | North East Lake Macquarie | GATESHEAD |  | 364 | 2.5842 | 135.633
D.F.ZN00222/033596 | D.F.ZN00222/033596 | 0 | North East Lake Macquarie | PELICAN |  | 400 | 3.394 | 178.138 | 1
D.F.ZN00222/033597 | D.F.ZN00222/033597 | 0 | North East Lake Macquarie | PELICAN |  | 398 | 2.4399 | 128.0603
D.F.ZN00222/033600 | D.F.ZN00222/033600 | 0 | North East Lake Macquarie | PELICAN |  | 224 | 2.2554 | 118.378
D.F.ZN00222/033601 | D.F.ZN00222/033601 | 0 | North East Lake Macquarie | PELICAN |  | 224 | 1.863 | 97.7811
D.F.ZN00222/033602 | D.F.ZN00222/033602 | 0 | North East Lake Macquarie | PELICAN |  | 307 | 3.1229 | 163.9121
D.F.ZN00223/014393 | D.F.ZN00223/014393 | 0 | North East Lake Macquarie | SWANSEA |  | 293 | 2.1811 | 114.4761
D.F.ZN00223/014394 | D.F.ZN00223/014394 | 0 | North East Lake Macquarie | SWANSEA |  | 298 | 3.626 | 190.3164
D.F.ZN00223/014395 | D.F.ZN00223/014395 | 0 | North East Lake Macquarie | SWANSEA |  | 323 | 1.5887 | 83.3856
D.F.ZN00223/014397 | D.F.ZN00223/014397 | 0 | North East Lake Macquarie | SWANSEA |  | 293 | 2.8368 | 148.8912
D.F.ZN00223/014398 | D.F.ZN00223/014398 | 0 | North East Lake Macquarie | SWANSEA |  | 325 | 2.4995 | 131.1896
D.F.ZN00223/014399 | D.F.ZN00223/014399 | 0 | North East Lake Macquarie | SWANSEA |  | 298 | 3.1191 | 163.7126
D.F.ZN00224/080326 | D.F.ZN00224/080326 | 0 | Newcastle Western Corridor | ARGENTON |  | 400 | 5.2571 | 275.9256
D.F.ZN00224/080328 | D.F.ZN00224/080328 | 0 | Newcastle Western Corridor | ARGENTON |  | 400 | 2.0528 | 107.7419
D.F.ZN00224/080329 | D.F.ZN00224/080329 | 0 | Newcastle Western Corridor | ARGENTON |  | 335 | 1.8538 | 97.301
D.F.ZN00224/080331 | D.F.ZN00224/080331 | 0 | Newcastle Western Corridor | ARGENTON |  | 400 | 3.2694 | 171.5987
D.F.ZN00224/080332 | D.F.ZN00224/080332 | 0 | Newcastle Western Corridor | ARGENTON |  | 398 | 4.6766 | 245.4592
D.F.ZN00224/080335 | D.F.ZN00224/080335 | 0 | Newcastle Western Corridor | ARGENTON |  | 335 | 1.462 | 76.7337
D.F.ZN00224/080337 | D.F.ZN00224/080337 | 0 | Newcastle Western Corridor | ARGENTON |  | 398 | 4.67 | 245.1138
D.F.ZN00224/080340 | D.F.ZN00224/080340 | 0 | Newcastle Western Corridor | ARGENTON |  | 398 | 3.5821 | 188.0131
D.F.ZN00224/080341 | D.F.ZN00224/080341 | 0 | Newcastle Western Corridor | ARGENTON |  | 400 | 3.5848 | 188.1507
D.F.ZN00224/080344 | D.F.ZN00224/080344 | 0 | Newcastle Western Corridor | ARGENTON |  | 308 | 4.3194 | 226.7095
D.F.ZN00224/080346 | D.F.ZN00224/080346 | 0 | Newcastle Western Corridor | ARGENTON |  | 400 | 6.1357 | 322.0402
D.F.ZN00227/013014 | D.F.ZN00227/013014 | 0 | West Lake Macquarie | AVONDALE |  | 308 | 0.2386 | 12.5224
D.F.ZN00227/013015 | D.F.ZN00227/013015 | 0 | West Lake Macquarie | AVONDALE |  | 301 | 3.3914 | 178.002
D.F.ZN00227/013016 | D.F.ZN00227/013016 | 0 | West Lake Macquarie | AVONDALE |  | 293 | 0.243 | 12.7564
D.F.ZN00227/013018 | D.F.ZN00227/013018 | 0 | West Lake Macquarie | AVONDALE |  | 318 | 2.33 | 122.2925
D.F.ZN00227/013019 | D.F.ZN00227/013019 | 0 | West Lake Macquarie | AVONDALE |  | 235 | 0.7087 | 37.1953
D.F.ZN00227/013020 | D.F.ZN00227/013020 | 0 | West Lake Macquarie | AVONDALE |  | 293 | 2.6852 | 140.9357
D.F.ZN00227/013021 | D.F.ZN00227/013021 | 0 | West Lake Macquarie | AVONDALE |  | 335 | 3.2256 | 169.2992
D.F.ZN00228/085407 | D.F.ZN00228/085407 | 0 | Port Stephens | STOCKTON |  | 307 | 0.0495 | 2.6003
D.F.ZN00228/085410 | D.F.ZN00228/085410 | 0 | Port Stephens | STOCKTON |  | 286 | 2.2994 | 120.6879
D.F.ZN00228/085413 | D.F.ZN00228/085413 | 0 | Port Stephens | STOCKTON |  | 286 | 4.888 | 256.5533
D.F.ZN00228/085415 | D.F.ZN00228/085415 | 0 | Port Stephens | STOCKTON |  | 293 | 1.9983 | 104.8825
D.F.ZN00229/034983 | D.F.ZN00229/034983 | 0 | Port Stephens | WILLIAMTOWN |  | 224 | 2.3272 | 122.1465 | 1 | CBZZN00229PA02 | PA2 | 34986
D.F.ZN00229/034986 | D.F.ZN00229/034986 | 0 | Port Stephens | WILLIAMTOWN |  | 148 | 0.2552 | 13.3925 | 1 | CBZZN00229PA04 | PA4 | 34992
D.F.ZN00229/034989 | D.F.ZN00229/034989 | 0 | Port Stephens | WILLIAMTOWN |  | 444 | 0.0811 | 4.2573 |  | CBZZN00229PA01 | PA1 | 34983
D.F.ZN00229/034992 | D.F.ZN00229/034992 | 0 | Port Stephens | WILLIAMTOWN |  | 484 | 0.5609 | 29.438 | 1
D.F.ZN00229/034995 | D.F.ZN00229/034995 | 0 | Port Stephens | WILLIAMTOWN |  | 444 | 2.474 | 129.849
D.F.ZN00230/081432 | D.F.ZN00230/081432 | 0 | Port Stephens | TANILBA BAY |  | 337 | 2.8707 | 150.6745 | 1
D.F.ZN00230/081434 | D.F.ZN00230/081434 | 0 | Port Stephens | TANILBA BAY |  | 335 | 3.4802 | 182.6647
D.F.ZN00230/081438 | D.F.ZN00230/081438 | 0 | Port Stephens | TANILBA BAY |  | 373 | 1.4552 | 76.3765
D.F.ZN00230/081440 | D.F.ZN00230/081440 | 0 | Port Stephens | TANILBA BAY |  | 337 | 3.4282 | 179.9332
D.F.ZN00232/011453 | D.F.ZN00232/011453 | 0 | Port Stephens | NELSON BAY |  | 286 | 2.7348 | 143.5372 |  | CBZZN00232PA03 | 232:33413
D.F.ZN00232/011454 | D.F.ZN00232/011454 | 0 | Port Stephens | NELSON BAY |  | 353 | 3.2914 | 172.7535 |  | CBZZN00232PA04 | 232:11455
D.F.ZN00232/011455 | D.F.ZN00232/011455 | 0 | Port Stephens | NELSON BAY |  | 282 | 4.4252 | 232.2618 | 1 | CBZZN00232PA05 | 232:33409
D.F.ZN00232/011457 | D.F.ZN00232/011457 | 0 | Port Stephens | NELSON BAY |  | 293 | 3.7356 | 196.0705 |  | CBZZN00232PA09 | 232:33407
D.F.ZN00232/011460 | D.F.ZN00232/011460 | 0 | Port Stephens | NELSON BAY |  | 293 | 3.231 | 169.5859
D.F.ZN00232/033407 | D.F.ZN00232/033407 | 0 | Port Stephens | NELSON BAY |  | 385 | 2.7967 | 146.7878 | 1
D.F.ZN00232/033409 | D.F.ZN00232/033409 | 0 | Port Stephens | NELSON BAY |  | 263 | 4.021 | 211.046 | 1
D.F.ZN00232/033413 | D.F.ZN00232/033413 | 0 | Port Stephens | NELSON BAY |  | 398 | 3.1078 | 163.1186 | 1
D.F.ZN00233/082812 | D.F.ZN00233/082812 | 0 | Port Stephens | MEDOWIE |  | 335 | 4.2446 | 222.7812
D.F.ZN00233/082813 | D.F.ZN00233/082813 | 0 | Port Stephens | MEDOWIE |  | 400 | 1.9068 | 100.0798
D.F.ZN00233/082815 | D.F.ZN00233/082815 | 0 | Port Stephens | MEDOWIE |  | 400 | 3.8633 | 202.7693
D.F.ZN00233/082818 | D.F.ZN00233/082818 | 0 | Port Stephens | MEDOWIE |  | 400 | 0.2155 | 11.3125
D.F.ZN00233/082819 | D.F.ZN00233/082819 | 0 | Port Stephens | MEDOWIE |  | 400 | 5.8622 | 307.685
D.F.ZN00233/082821 | D.F.ZN00233/082821 | 0 | Port Stephens | MEDOWIE |  | 335 | 1.171 | 61.4621
D.F.ZN00235/002120 | D.F.ZN00235/002120 | 0 | Maitland | TARRO | 1 | 300 | 1.854 | 97.3117
D.F.ZN00235/002123 | D.F.ZN00235/002123 | 0 | Maitland | TARRO | 1 | 300 | 3.7682 | 197.7787
D.F.ZN00235/002124 | D.F.ZN00235/002124 | 0 | Maitland | TARRO | 1 | 300 | 2.3549 | 123.6004
D.F.ZN00235/002728 | D.F.ZN00235/002728 | 0 | Maitland | TARRO | 1 | 300 | 6.7664 | 355.1439
D.F.ZN00235/008684 | D.F.ZN00235/008684 | 0 | Maitland | TARRO | 1 | 300 | 2.8084 | 147.4052
D.F.ZN00235/008685 | D.F.ZN00235/008685 | 0 | Maitland | TARRO | 1 | 300 | 0.2214 | 11.6225
D.F.ZN00235/085878 | D.F.ZN00235/085878 | 0 | Maitland | TARRO |  | 300 |  | 0
D.F.ZN00235/085879 | D.F.ZN00235/085879 | 0 | Maitland | TARRO |  | 280 | 3.0093 | 157.9473
D.F.ZN00235/085881 | D.F.ZN00235/085881 | 0 | Maitland | TARRO |  | 400 | 2.51 | 131.7413
D.F.ZN00235/085882 | D.F.ZN00235/085882 | 0 | Maitland | TARRO |  | 271 | 7.7472 | 406.6203
D.F.ZN00235/085886 | D.F.ZN00235/085886 | 0 | Maitland | TARRO |  | 400 |  | 0
D.F.ZN00235/085888 | D.F.ZN00235/085888 | 0 | Maitland | TARRO |  | 336 | 0.2687 | 14.1019
D.F.ZN00235/085889 | D.F.ZN00235/085889 | 0 | Maitland | TARRO |  | 400 | 4.4776 | 235.0156
D.F.ZN00235/085890 | D.F.ZN00235/085890 | 0 | Maitland | TARRO |  | 400 |  | 0
D.F.ZN00238/034136 | D.F.ZN00238/034136 | 0 | Maitland | THORNTON |  | 290 | 6.0616 | 318.1494 | 1 | CBZZN00238PA18 | 238:34136
D.F.ZN00238/034137 | D.F.ZN00238/034137 | 0 | Maitland | THORNTON |  | 350 | 2.6019 | 136.5664 |  | CBZZN00238PA20 | 238:34141
D.F.ZN00238/034138 | D.F.ZN00238/034138 | 0 | Maitland | THORNTON |  | 400 | 3.5705 | 187.4021 |  | CBZZN00238PA11 | 238:34151
D.F.ZN00238/034140 | D.F.ZN00238/034140 | 0 | Maitland | THORNTON |  | 380 | 1.8704 | 98.171 |  | CBZZN00238PA04 | 238:34148
D.F.ZN00238/034141 | D.F.ZN00238/034141 | 0 | Maitland | THORNTON |  | 380 | 4.804 | 252.1432 | 1
D.F.ZN00238/034143 | D.F.ZN00238/034143 | 0 | Maitland | THORNTON |  | 350 | 3.8177 | 200.379
D.F.ZN00238/034144 | D.F.ZN00238/034144 | 0 | Maitland | THORNTON |  | 400 | 4.2617 | 223.6819
D.F.ZN00238/034147 | D.F.ZN00238/034147 | 0 | Maitland | THORNTON |  | 350 | 0.1954 | 10.2559
D.F.ZN00238/034148 | D.F.ZN00238/034148 | 0 | Maitland | THORNTON |  | 383 | 3.3159 | 174.0373 | 1
D.F.ZN00238/034150 | D.F.ZN00238/034150 | 0 | Maitland | THORNTON |  | 400 | 5.9053 | 309.9497
D.F.ZN00238/034151 | D.F.ZN00238/034151 | 0 | Maitland | THORNTON |  | 310 | 4.2487 | 223.0002 | 1
D.F.ZN00239/082127 | D.F.ZN00239/082127 | 0 | West Lake Macquarie | RATHMINES |  | 400 | 0.4328 | 22.7186
D.F.ZN00239/082128 | D.F.ZN00239/082128 | 0 | West Lake Macquarie | RATHMINES |  | 335 | 1.6006 | 84.0111
D.F.ZN00239/082129 | D.F.ZN00239/082129 | 0 | West Lake Macquarie | RATHMINES |  | 288 | 3.7579 | 197.2378 | 1
D.F.ZN00239/082131 | D.F.ZN00239/082131 | 0 | West Lake Macquarie | RATHMINES |  | 312 | 0.5872 | 30.8182
D.F.ZN00239/082132 | D.F.ZN00239/082132 | 0 | West Lake Macquarie | RATHMINES |  | 307 | 2.8923 | 151.8049
D.F.ZN00239/082133 | D.F.ZN00239/082133 | 0 | West Lake Macquarie | RATHMINES |  | 180 | 3.747 | 196.6685
D.F.ZN00239/082136 | D.F.ZN00239/082136 | 0 | West Lake Macquarie | RATHMINES |  | 307 | 2.6131 | 137.1512
D.F.ZN00240/34835L | D.F.ZN00240/034835 | 0 | Newcastle Ports | MAYFIELD WEST |  | 335 | 3.4424 | 180.6767
D.F.ZN00240/34840L | D.F.ZN00240/034840 | 0 | Newcastle Ports | MAYFIELD WEST |  | 400 | 3.8395 | 201.5225
D.F.ZN00240/34841L | D.F.ZN00240/034841 | 0 | Newcastle Ports | MAYFIELD WEST |  | 400 | 74.6571 | 3918.4815
D.F.ZN00240/34843L | D.F.ZN00240/034843 | 0 | Newcastle Ports | MAYFIELD WEST |  | 400 | 2.3328 | 122.4383
D.F.ZN00240/34846L | D.F.ZN00240/034846 | 0 | Newcastle Ports | MAYFIELD WEST |  | 290 | 3.3647 | 176.6003
D.F.ZN00240/34847L | D.F.ZN00240/034847 | 0 | Newcastle Ports | MAYFIELD WEST |  | 293 | 4.3879 | 230.3032
D.F.ZN00240/34849L | D.F.ZN00240/034849 | 0 | Newcastle Ports | MAYFIELD WEST |  | 400 | 5.7881 | 303.7952
D.F.ZN00240/34852L | D.F.ZN00240/034852 | 0 | Newcastle Ports | MAYFIELD WEST |  | 290 | 3.7418 | 196.3959
D.F.ZN00242/081532 | D.F.ZN00242/081532 | 0 | Port Stephens | TOMAREE |  | 400 | 1.9558 | 102.6533
D.F.ZN00242/081533 | D.F.ZN00242/081533 | 0 | Port Stephens | TOMAREE |  | 400 | 0.2915 | 15.2993
D.F.ZN00242/081535 | D.F.ZN00242/081535 | 0 | Port Stephens | TOMAREE |  | 400 | 3.2234 | 169.1848
D.F.ZN00242/081538 | D.F.ZN00242/081538 | 0 | Port Stephens | TOMAREE |  | 400 | 2.4685 | 129.5651
D.F.ZN00242/081539 | D.F.ZN00242/081539 | 0 | Port Stephens | TOMAREE |  | 400 | 4.1425 | 217.4266 | 1
D.F.ZN00242/081541 | D.F.ZN00242/081541 | 0 | Port Stephens | TOMAREE |  | 398 | 3.0243 | 158.7323
D.F.ZN00243/80074L | D.F.ZN00243/080074 | 0 | West Lake Macquarie | MORISSET |  | 400 | 3.7257 | 195.5495
D.F.ZN00243/80074R | D.F.ZN00243/080074 | 1 | West Lake Macquarie | MORISSET |  | 400 | 2.5436 | 133.5033
D.F.ZN00243/080075 | D.F.ZN00243/080075 | 0 | West Lake Macquarie | MORISSET |  | 364 | 4.7907 | 251.4478 | 1
D.F.ZN00243/080077 | D.F.ZN00243/080077 | 0 | West Lake Macquarie | MORISSET |  | 335 | 1.6424 | 86.2041
D.F.ZN00243/80078L | D.F.ZN00243/080078 | 0 | West Lake Macquarie | MORISSET |  | 400 | 3.8055 | 199.7372
D.F.ZN00243/80080L | D.F.ZN00243/080080 | 0 | West Lake Macquarie | MORISSET |  | 400 | 3.5976 | 188.8234
D.F.ZN00243/080081 | D.F.ZN00243/080081 | 0 | West Lake Macquarie | MORISSET |  | 400 | 4.6826 | 245.7747
D.F.ZN00243/080083 | D.F.ZN00243/080083 | 0 | West Lake Macquarie | MORISSET |  | 400 | 3.1497 | 165.3158
D.F.ZN00243/80084L | D.F.ZN00243/080084 | 0 | West Lake Macquarie | MORISSET |  | 298 | 2.8411 | 149.118
D.F.ZN00245/000072 | D.F.ZN00245/000072 | 0 | West Lake Macquarie | MYUNA |  |  | 7.9176 | 415.5675
D.F.ZN00246/000062 | D.F.ZN00246/000062 | 0 | West Lake Macquarie | COORANBONG |  |  | 3.3472 | 175.6807
D.F.ZN00250/091509 | D.F.ZN00250/091509 | 0 | #N/A | NEWSTAN COLLIERY SUBSTATION |  |  | 4.9393 | 259.2481
D.F.ZN00256/080632 | D.F.ZN00256/080632 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 3.1747 | 166.6281
D.F.ZN00256/080635 | D.F.ZN00256/080635 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 5.5839 | 293.0802
D.F.ZN00256/080638 | D.F.ZN00256/080638 | 0 | Newcastle Inner City | ADAMSTOWN |  | 307 | 3.2606 | 171.1369
D.F.ZN00256/080640 | D.F.ZN00256/080640 | 0 | Newcastle Inner City | ADAMSTOWN |  | 263 | 2.5863 | 135.7475
D.F.ZN00256/80641L | D.F.ZN00256/080641 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 8.0092 | 420.3738
D.F.ZN00256/080644 | D.F.ZN00256/080644 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 2.9405 | 154.3341
D.F.ZN00256/080646 | D.F.ZN00256/080646 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 4.5347 | 238.0126
D.F.ZN00256/80647L | D.F.ZN00256/080647 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 5.4919 | 288.2511
D.F.ZN00256/080650 | D.F.ZN00256/080650 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 4.2918 | 225.2614
D.F.ZN00256/080652 | D.F.ZN00256/080652 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 0.8199 | 43.0322
D.F.ZN00256/80653L | D.F.ZN00256/080653 | 0 | Newcastle Inner City | ADAMSTOWN |  | 400 | 1.6049 | 84.2336
D.F.ZN00257/081985 | D.F.ZN00257/081985 | 0 | Newcastle Inner City | BROADMEADOW |  | 189 | 1.9063 | 100.0528
D.F.ZN00257/081987 | D.F.ZN00257/081987 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 6.3031 | 330.8252
D.F.ZN00257/081988 | D.F.ZN00257/081988 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 2.8733 | 150.8084
D.F.ZN00257/081991 | D.F.ZN00257/081991 | 0 | Newcastle Inner City | BROADMEADOW |  | 286 | 2.1226 | 111.4081
D.F.ZN00257/081993 | D.F.ZN00257/081993 | 0 | Newcastle Inner City | BROADMEADOW |  | 286 | 1.1002 | 57.7455
D.F.ZN00257/081994 | D.F.ZN00257/081994 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 3.7211 | 195.3053
D.F.ZN00257/081997 | D.F.ZN00257/081997 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 1.8003 | 94.493
D.F.ZN00257/081999 | D.F.ZN00257/081999 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 3.4321 | 180.1395
D.F.ZN00257/082000 | D.F.ZN00257/082000 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 1.7575 | 92.246
D.F.ZN00257/082003 | D.F.ZN00257/082003 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 1.7268 | 90.6333
D.F.ZN00257/082006 | D.F.ZN00257/082006 | 0 | Newcastle Inner City | BROADMEADOW |  | 400 | 1.3815 | 72.5094
D.F.ZN00258/080773 | D.F.ZN00258/080773 | 0 | Newcastle Ports | JESMOND |  | 286 | 2.4122 | 126.6091
D.F.ZN00258/080775 | D.F.ZN00258/080775 | 0 | Newcastle Ports | JESMOND |  | 307 | 4.6536 | 244.2503
D.F.ZN00258/80776L | D.F.ZN00258/080776 | 0 | Newcastle Ports | JESMOND |  | 335 | 1.1086 | 58.186
D.F.ZN00258/080778 | D.F.ZN00258/080778 | 0 | Newcastle Ports | JESMOND |  | 400 | 2.5433 | 133.4896
D.F.ZN00258/080779 | D.F.ZN00258/080779 | 0 | Newcastle Ports | JESMOND |  | 335 | 3.3559 | 176.1415
D.F.ZN00258/080781 | D.F.ZN00258/080781 | 0 | Newcastle Ports | JESMOND |  | 400 | 5.0524 | 265.1813
D.F.ZN00258/80782L | D.F.ZN00258/080782 | 0 | Newcastle Ports | JESMOND |  | 400 | 4.5803 | 240.4027
D.F.ZN00258/80784L | D.F.ZN00258/080784 | 0 | Newcastle Ports | JESMOND |  | 400 | 5.0209 | 263.5297
D.F.ZN00258/080785 | D.F.ZN00258/080785 | 0 | Newcastle Ports | JESMOND |  | 286 | 0.1264 | 6.6338
D.F.ZN00258/080787 | D.F.ZN00258/080787 | 0 | Newcastle Ports | JESMOND |  | 400 | 5.5912 | 293.4624
D.F.ZN00258/80790L | D.F.ZN00258/080790 | 0 | Newcastle Ports | JESMOND |  | 335 | 2.4306 | 127.5724
D.F.ZN00258/080791 | D.F.ZN00258/080791 | 0 | Newcastle Ports | JESMOND |  | 400 | 2.1414 | 112.3958
D.F.ZN00258/080793 | D.F.ZN00258/080793 | 0 | Newcastle Ports | JESMOND |  | 400 | 5.1996 | 272.907
D.F.ZN00258/80794L | D.F.ZN00258/080794 | 0 | Newcastle Ports | JESMOND |  | 400 | 4.665 | 244.8474
D.F.ZN00261/081864 | D.F.ZN00261/081864 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 400 | 3.3087 | 173.6597
D.F.ZN00261/081865 | D.F.ZN00261/081865 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 386 | 3.9101 | 205.226
D.F.ZN00261/081867 | D.F.ZN00261/081867 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 286 | 1.3221 | 69.3906
D.F.ZN00261/081870 | D.F.ZN00261/081870 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 400 | 5.0744 | 266.3377
D.F.ZN00261/081874 | D.F.ZN00261/081874 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 351 | 4.5233 | 237.4098
D.F.ZN00261/081876 | D.F.ZN00261/081876 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 286 | 2.6861 | 140.9836
D.F.ZN00261/081877 | D.F.ZN00261/081877 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 263 | 1.0099 | 53.0065
D.F.ZN00261/081879 | D.F.ZN00261/081879 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 400 | 7.3172 | 384.0535 | 1
D.F.ZN00261/081882 | D.F.ZN00261/081882 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 400 | 4.589 | 240.8618
D.F.ZN00261/081885 | D.F.ZN00261/081885 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 293 | 3.2253 | 169.2823
D.F.ZN00261/081886 | D.F.ZN00261/081886 | 0 | North East Lake Macquarie | CHARLESTOWN |  | 400 | 2.6397 | 138.547
D.F.ZN00262/000005 | D.F.ZN00262/000005 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 3.5574 | 186.7149
D.F.ZN00262/000006 | D.F.ZN00262/000006 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 300 | 2.4356 | 127.8335
D.F.ZN00262/000007 | D.F.ZN00262/000007 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 3.8663 | 202.9267
D.F.ZN00262/000008 | D.F.ZN00262/000008 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 2.6925 | 141.3212
D.F.ZN00262/000013 | D.F.ZN00262/000013 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 335 | 1.5706 | 82.4332
D.F.ZN00262/000014 | D.F.ZN00262/000014 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 300 | 0.6689 | 35.1082
D.F.ZN00262/000015 | D.F.ZN00262/000015 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 1.6677 | 87.5304
D.F.ZN00262/000016 | D.F.ZN00262/000016 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 385 | 4.5054 | 236.4704
D.F.ZN00262/000017 | D.F.ZN00262/000017 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 2.4623 | 129.2364
D.F.ZN00262/000019 | D.F.ZN00262/000019 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 350 | 2.8954 | 151.9717
D.F.ZN00262/000020 | D.F.ZN00262/000020 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 205 | 1.6555 | 86.8905
D.F.ZN00262/000021 | D.F.ZN00262/000021 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 340 | 1.6718 | 87.7473
D.F.ZN00262/000025 | D.F.ZN00262/000025 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 1.3065 | 68.5736
D.F.ZN00262/000026 | D.F.ZN00262/000026 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 300 | 1.7408 | 91.368
D.F.ZN00262/000027 | D.F.ZN00262/000027 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 1.8098 | 94.9908
D.F.ZN00262/000028 | D.F.ZN00262/000028 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 3.3342 | 174.9994
D.F.ZN00262/000029 | D.F.ZN00262/000029 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 205 | 0.9713 | 50.9775
D.F.ZN00262/000030 | D.F.ZN00262/000030 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 3.5875 | 188.2926
D.F.ZN00262/000031 | D.F.ZN00262/000031 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 230 | 3.7946 | 199.166
D.F.ZN00262/000032 | D.F.ZN00262/000032 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 285 | 1.736 | 91.1167
D.F.ZN00262/000033 | D.F.ZN00262/000033 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 0.3192 | 16.7539
D.F.ZN00262/000034 | D.F.ZN00262/000034 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 1.9326 | 101.4374
D.F.ZN00262/000039 | D.F.ZN00262/000039 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 400 | 2.1819 | 114.5214
D.F.ZN00262/000040 | D.F.ZN00262/000040 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 230 | 2.079 | 109.1171
D.F.ZN00262/000041 | D.F.ZN00262/000041 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 315 | 2.2299 | 117.0395
D.F.ZN00262/000042 | D.F.ZN00262/000042 | 0 | Eastern Suburbs Inner | MARRICKVILLE |  | 315 | 3.4791 | 182.6075
D.F.ZN00263/00033L | D.F.ZN00263/000033 | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 0.2989 | 15.6861
D.F.ZN00263/00034L | D.F.ZN00263/000034 | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 0.2175 | 11.4178
D.F.ZN00263/00031H | D.F.ZN00263/00031H | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 0.3003 | 15.7618
D.F.ZN00263/00032D | D.F.ZN00263/00032D | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 2.3594 | 123.8354
D.F.ZN00263/00033K | D.F.ZN00263/00033K | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 1.6915 | 88.7799
D.F.ZN00263/00033M | D.F.ZN00263/00033M | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 0.4326 | 22.7053
D.F.ZN00263/00034K | D.F.ZN00263/00034K | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 0.5712 | 29.9795
D.F.ZN00263/00034M | D.F.ZN00263/00034M | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 1.5259 | 80.0877
D.F.ZN00263/00037E | D.F.ZN00263/00037E | 0 | Sydney CBD | DALLEY ST |  |  |  | 0
D.F.ZN00263/00037F | D.F.ZN00263/00037F | 0 | Sydney CBD | DALLEY ST | 1 | 300 | 5.1453 | 270.0576
D.F.ZN00264/81231R | D.F.ZN00264/081231 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 3.1026 | 162.8421
D.F.ZN00264/81232R | D.F.ZN00264/081232 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 2.852 | 149.6891
D.F.ZN00264/81232L | D.F.ZN00264/081232 | 1 | Port Stephens | RAYMOND TERRACE |  | 308 | 0.9661 | 50.7062 | 1
D.F.ZN00264/81233L | D.F.ZN00264/081233 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 2.4821 | 130.2747
D.F.ZN00264/81236L | D.F.ZN00264/081236 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 5.0918 | 267.2512
D.F.ZN00264/081238 | D.F.ZN00264/081238 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 1.6696 | 87.6289
D.F.ZN00264/81240L | D.F.ZN00264/081240 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 1.4335 | 75.2407
D.F.ZN00264/81240R | D.F.ZN00264/081240 | 1 | Port Stephens | RAYMOND TERRACE |  | 383 | 0.7309 | 38.362
D.F.ZN00264/81241L | D.F.ZN00264/081241 | 0 | Port Stephens | RAYMOND TERRACE |  | 383 | 3.1146 | 163.472
D.F.ZN00264/81241R | D.F.ZN00264/081241 | 1 | Port Stephens | RAYMOND TERRACE |  | 400 | 1.1327 | 59.4517
D.F.ZN00264/81244L | D.F.ZN00264/081244 | 0 | Port Stephens | RAYMOND TERRACE |  | 400 | 4.9274 | 258.6229
D.F.ZN00265/081641 | D.F.ZN00265/081641 | 0 | Port Stephens | TOMAGO |  | 400 | 4.6369 | 243.3732
D.F.ZN00265/081645 | D.F.ZN00265/081645 | 0 | Port Stephens | TOMAGO |  | 400 | 2.7281 | 143.19
D.F.ZN00265/081648 | D.F.ZN00265/081648 | 0 | Port Stephens | TOMAGO |  | 400 | 2.6471 | 138.9362
D.F.ZN00265/81649L | D.F.ZN00265/081649 | 0 | Port Stephens | TOMAGO |  | 400 | 1.7705 | 92.928
D.F.ZN00265/81651L | D.F.ZN00265/081651 | 0 | Port Stephens | TOMAGO |  | 400 | 2.6409 | 138.6094
D.F.ZN00270/083583 | D.F.ZN00270/083583 | 0 | West Lake Macquarie | TORONTO WEST |  | 400 | 1.5787 | 82.8628
D.F.ZN00270/083584 | D.F.ZN00270/083584 | 0 | West Lake Macquarie | TORONTO WEST |  | 351 | 1.9582 | 102.7764
D.F.ZN00270/083586 | D.F.ZN00270/083586 | 0 | West Lake Macquarie | TORONTO WEST |  | 400 | 2.2236 | 116.707
D.F.ZN00270/083587 | D.F.ZN00270/083587 | 0 | West Lake Macquarie | TORONTO WEST |  | 335 | 3.866 | 202.912 | 1
D.F.ZN00270/083590 | D.F.ZN00270/083590 | 0 | West Lake Macquarie | TORONTO WEST |  | 307 | 3.6373 | 190.9062
D.F.ZN00270/083591 | D.F.ZN00270/083591 | 0 | West Lake Macquarie | TORONTO WEST |  | 400 | 3.6257 | 190.2981
D.F.ZN00270/083593 | D.F.ZN00270/083593 | 0 | West Lake Macquarie | TORONTO WEST |  | 400 | 1.8639 | 97.8318
D.F.ZN00270/083594 | D.F.ZN00270/083594 | 0 | West Lake Macquarie | TORONTO WEST |  | 400 | 3.1031 | 162.8691
D.F.ZN00340/000003 | D.F.ZN00340/000003 | 0 | Eastern Suburbs Outer | BOTANY |  | 400 | 2.2733 | 119.3188
D.F.ZN00340/000004 | D.F.ZN00340/000004 | 0 | Eastern Suburbs Outer | BOTANY |  | 210 | 0.9259 | 48.5955
D.F.ZN00340/000008 | D.F.ZN00340/000008 | 0 | Eastern Suburbs Outer | BOTANY |  | 360 | 1.6425 | 86.2086
D.F.ZN00340/000009 | D.F.ZN00340/000009 | 0 | Eastern Suburbs Outer | BOTANY |  | 400 | 1.775 | 93.1645
D.F.ZN00340/000010 | D.F.ZN00340/000010 | 0 | Eastern Suburbs Outer | BOTANY |  | 255 | 1.5844 | 83.1585
D.F.ZN00340/000011 | D.F.ZN00340/000011 | 0 | Eastern Suburbs Outer | BOTANY |  | 175 | 0.833 | 43.721
D.F.ZN00340/000032 | D.F.ZN00340/000032 | 0 | Eastern Suburbs Outer | BOTANY |  | 400 | 2.355 | 123.6032
D.F.ZN00340/000034 | D.F.ZN00340/000034 | 0 | Eastern Suburbs Outer | BOTANY |  | 370 | 0.7792 | 40.8962
D.F.ZN00340/000035 | D.F.ZN00340/000035 | 0 | Eastern Suburbs Outer | BOTANY |  | 275 | 2.8233 | 148.1849
D.F.ZN00340/000037 | D.F.ZN00340/000037 | 0 | Eastern Suburbs Outer | BOTANY |  | 285 | 4.6275 | 242.8821
D.F.ZN00340/000040 | D.F.ZN00340/000040 | 0 | Eastern Suburbs Outer | BOTANY |  | 250 | 1.3847 | 72.6762
D.F.ZN00340/000042 | D.F.ZN00340/000042 | 0 | Eastern Suburbs Outer | BOTANY |  | 285 | 1.5201 | 79.7859
D.F.ZN00340/000044 | D.F.ZN00340/000044 | 0 | Eastern Suburbs Outer | BOTANY |  | 195 | 2.7784 | 145.8303
D.F.ZN00340/000045 | D.F.ZN00340/000045 | 0 | Eastern Suburbs Outer | BOTANY |  | 195 | 2.5541 | 134.0565
D.F.ZN00342/000015 | D.F.ZN00342/000015 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 265 | 1.4951 | 78.4714
D.F.ZN00342/00016L | D.F.ZN00342/000016 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 285 | 1.8116 | 95.0843
D.F.ZN00342/00016R | D.F.ZN00342/000016 | 1 | Eastern Suburbs Outer | PADDINGTON |  | 245 | 1.141 | 59.8851
D.F.ZN00342/000017 | D.F.ZN00342/000017 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 265 | 3.3811 | 177.46
D.F.ZN00342/00018L | D.F.ZN00342/000018 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 305 | 2.6457 | 138.8633
D.F.ZN00342/00018R | D.F.ZN00342/000018 | 1 | Eastern Suburbs Outer | PADDINGTON |  | 365 | 0.6485 | 34.0367
D.F.ZN00342/000021 | D.F.ZN00342/000021 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 260 | 2.1056 | 110.5135
D.F.ZN00342/00022L | D.F.ZN00342/000022 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 305 | 3.3876 | 177.8004
D.F.ZN00342/000023 | D.F.ZN00342/000023 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 280 | 2.9106 | 152.7677
D.F.ZN00342/00024L | D.F.ZN00342/000024 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 265 | 2.0354 | 106.8308
D.F.ZN00342/00024R | D.F.ZN00342/000024 | 1 | Eastern Suburbs Outer | PADDINGTON |  | 275 | 0.285 | 14.9601
D.F.ZN00342/000025 | D.F.ZN00342/000025 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 400 | 2.404 | 126.1771
D.F.ZN00342/00026R | D.F.ZN00342/000026 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 325 | 2.5928 | 136.0862
D.F.ZN00342/00026L | D.F.ZN00342/000026 | 1 | Eastern Suburbs Outer | PADDINGTON |  | 285 | 1.6006 | 84.0074
D.F.ZN00342/000027 | D.F.ZN00342/000027 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 240 | 0.67 | 35.1676
D.F.ZN00342/00028R | D.F.ZN00342/000028 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 265 | 2.4539 | 128.7986
D.F.ZN00342/00028L | D.F.ZN00342/000028 | 1 | Eastern Suburbs Outer | PADDINGTON |  | 260 | 2.0985 | 110.1449
D.F.ZN00342/000032 | D.F.ZN00342/000032 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 400 | 1.8629 | 97.7753
D.F.ZN00342/00033L | D.F.ZN00342/000033 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 260 | 1.9894 | 104.4142
D.F.ZN00342/000035 | D.F.ZN00342/000035 | 0 | Eastern Suburbs Outer | PADDINGTON |  | 265 | 1.3033 | 68.4078
D.F.ZN00384/000002 | D.F.ZN00384/000002 | 0 | Camperdown | CAMPERDOWN |  | 350 | 1.5927 | 83.5955
D.F.ZN00384/000004 | D.F.ZN00384/000004 | 0 | Camperdown | CAMPERDOWN |  | 350 | 0.637 | 33.4329
D.F.ZN00384/000022 | D.F.ZN00384/000022 | 0 | Camperdown | CAMPERDOWN |  | 365 | 0.5103 | 26.7847
D.F.ZN00384/000032 | D.F.ZN00384/000032 | 0 | Camperdown | CAMPERDOWN |  | 325 | 0.3039 | 15.952
D.F.ZN00384/00062L | D.F.ZN00384/000062 | 0 | Camperdown | CAMPERDOWN |  | 400 | 1.0823 | 56.8076
D.F.ZN00384/000063 | D.F.ZN00384/000063 | 0 | Camperdown | CAMPERDOWN |  | 400 | 0.9218 | 48.383
D.F.ZN00384/00065L | D.F.ZN00384/000065 | 0 | Camperdown | CAMPERDOWN |  | 325 | 4.0965 | 215.0114
D.F.ZN00384/00065R | D.F.ZN00384/000065 | 1 | Camperdown | CAMPERDOWN |  | 400 | 0.2664 | 13.9846
D.F.ZN00384/000066 | D.F.ZN00384/000066 | 0 | Camperdown | CAMPERDOWN |  | 400 | 1.2685 | 66.5806
D.F.ZN00384/00068L | D.F.ZN00384/000068 | 0 | Camperdown | CAMPERDOWN |  | 315 | 0.9879 | 51.8503
D.F.ZN00384/000069 | D.F.ZN00384/000069 | 0 | Camperdown | CAMPERDOWN |  | 400 | 2.8035 | 147.1475
D.F.ZN00384/00070L | D.F.ZN00384/000070 | 0 | Camperdown | CAMPERDOWN |  | 400 | 1.9008 | 99.7637
D.F.ZN00384/00070R | D.F.ZN00384/000070 | 1 | Camperdown | CAMPERDOWN |  | 350 | 1.1289 | 59.2537
D.F.ZN00384/000071 | D.F.ZN00384/000071 | 0 | Camperdown | CAMPERDOWN |  | 400 | 0.843 | 44.2486
D.F.ZN00384/00073L | D.F.ZN00384/000073 | 0 | Camperdown | CAMPERDOWN |  | 400 | 1.9677 | 103.2776
D.F.ZN00384/000074 | D.F.ZN00384/000074 | 0 | Camperdown | CAMPERDOWN |  | 375 | 1.5841 | 83.1433
D.F.ZN00384/00075L | D.F.ZN00384/000075 | 0 | Camperdown | CAMPERDOWN |  | 325 | 2.3308 | 122.3344
D.F.ZN00384/000076 | D.F.ZN00384/000076 | 0 | Camperdown | CAMPERDOWN |  | 400 | 3.9458 | 207.1013
D.F.ZN00384/000079 | D.F.ZN00384/000079 | 0 | Camperdown | CAMPERDOWN |  | 400 | 3.3579 | 176.2446
D.F.ZN00384/00080L | D.F.ZN00384/000080 | 0 | Camperdown | CAMPERDOWN |  | 400 | 0.8073 | 42.374
D.F.ZN00384/00080R | D.F.ZN00384/000080 | 1 | Camperdown | CAMPERDOWN |  | 400 | 0.429 | 22.518
D.F.ZN00384/000081 | D.F.ZN00384/000081 | 0 | Camperdown | CAMPERDOWN |  | 400 | 0.7011 | 36.7962
D.F.ZN00502/048001 | D.F.ZN00502/048001 | 0 | Maitland | TELARAH |  | 295 | 3.8678 | 203.0049 | 1 | CBZZN00502PA08 | 502:48004
D.F.ZN00502/048002 | D.F.ZN00502/048002 | 0 | Maitland | TELARAH |  | 300 | 0.8278 | 43.4484 |  | CBZZN00502PA10 | 502:48001
D.F.ZN00502/048004 | D.F.ZN00502/048004 | 0 | Maitland | TELARAH |  | 295 | 4.7097 | 247.1958 | 1
D.F.ZN00502/048008 | D.F.ZN00502/048008 | 0 | Maitland | TELARAH |  | 295 | 1.9492 | 102.3071
D.F.ZN00502/048009 | D.F.ZN00502/048009 | 0 | Maitland | TELARAH |  | 260 | 4.2393 | 222.5033
D.F.ZN00502/048010 | D.F.ZN00502/048010 | 0 | Maitland | TELARAH |  | 315 | 3.4609 | 181.6478
D.F.ZN00507/080914 | D.F.ZN00507/080914 | 0 | Greater Cessnock | KURRI |  | 400 | 5.8351 | 306.2612 | 1 | ZN00507 | CBZZN00507PA06 | PA6 | 507:80932 | KURRI 132/11kV | Greater Cessnock | 162 | 150 | Kurri Kurri
D.F.ZN00507/080917 | D.F.ZN00507/080917 | 0 | Greater Cessnock | KURRI |  | 400 | 2.6776 | 140.5358 |  | ZN00507 | CBZZN00507PA12 | PA12 | 507:80914 | KURRI 132/11kV | Greater Cessnock | 50 | 50 | Heddon Greta
D.F.ZN00507/080920 | D.F.ZN00507/080920 | 0 | Greater Cessnock | KURRI |  | 400 | 0.5977 | 31.3732 |  | ZN00507 | CBZZN00507PA19 | PA19 | 507:80923 | KURRI 132/11kV | Greater Cessnock | 114.5858 | 114.5858 | Gillieston Heights
D.F.ZN00507/080922 | D.F.ZN00507/080922 | 0 | Greater Cessnock | KURRI |  | 400 | 4.2869 | 225.0031
D.F.ZN00507/080923 | D.F.ZN00507/080923 | 0 | Greater Cessnock | KURRI |  | 400 | 6.2611 | 328.6235 | 1
D.F.ZN00507/080925 | D.F.ZN00507/080925 | 0 | Greater Cessnock | KURRI |  | 400 | 4.6242 | 242.7082
D.F.ZN00507/080926 | D.F.ZN00507/080926 | 0 | Greater Cessnock | KURRI |  | 400 | 4.4226 | 232.1251
D.F.ZN00507/080931 | D.F.ZN00507/080931 | 0 | Greater Cessnock | KURRI |  | 230 | 3.0673 | 160.9941
D.F.ZN00507/080932 | D.F.ZN00507/080932 | 0 | Greater Cessnock | KURRI |  | 400 | 4.6059 | 241.7493 | 1
D.F.ZN00508/082574 | D.F.ZN00508/082574 | 0 | Maitland | BRANDY HILL |  | 400 | 1.437 | 75.4232
D.F.ZN00508/082575 | D.F.ZN00508/082575 | 0 | Maitland | BRANDY HILL |  | 400 | 1.8368 | 96.4077
D.F.ZN00508/082576 | D.F.ZN00508/082576 | 0 | Maitland | BRANDY HILL |  | 400 | 2.6517 | 139.1773
D.F.ZN00508/082578 | D.F.ZN00508/082578 | 0 | Maitland | BRANDY HILL |  | 400 | 2.0327 | 106.6885
D.F.ZN00508/082579 | D.F.ZN00508/082579 | 0 | Maitland | BRANDY HILL |  | 335 | 1.0255 | 53.8255
D.F.ZN00508/082580 | D.F.ZN00508/082580 | 0 | Maitland | BRANDY HILL |  | 400 | 1.7864 | 93.7597
D.F.ZN00509/033395 | D.F.ZN00509/033395 | 0 | Greater Cessnock | PAXTON |  | 300 | 1.8855 | 98.965
D.F.ZN00509/033397 | D.F.ZN00509/033397 | 0 | Greater Cessnock | PAXTON |  | 180 | 1.1692 | 61.365
D.F.ZN00509/033399 | D.F.ZN00509/033399 | 0 | Greater Cessnock | PAXTON |  | 240 | 3.3155 | 174.0209
D.F.ZN00511/029869 | D.F.ZN00511/029869 | 0 | Maitland | RUTHERFORD |  | 350 | 1.5179 | 79.6712 |  | CBZZN00511PA02 | 511:29873
D.F.ZN00511/029870 | D.F.ZN00511/029870 | 0 | Maitland | RUTHERFORD |  | 400 | 2.7072 | 142.0911 |  | CBZZN00511PA03 | 511:29880
D.F.ZN00511/029872 | D.F.ZN00511/029872 | 0 | Maitland | RUTHERFORD |  | 380 | 3.9634 | 208.0258 |  | CBZZN00511PA09 | 511:29876
D.F.ZN00511/029873 | D.F.ZN00511/029873 | 0 | Maitland | RUTHERFORD |  | 350 | 6.9788 | 366.2901 | 1
D.F.ZN00511/029874 | D.F.ZN00511/029874 | 0 | Maitland | RUTHERFORD |  | 350 | 1.9227 | 100.9173
D.F.ZN00511/029876 | D.F.ZN00511/029876 | 0 | Maitland | RUTHERFORD |  | 350 | 3.072 | 161.238 | 1
D.F.ZN00511/029877 | D.F.ZN00511/029877 | 0 | Maitland | RUTHERFORD |  | 380 | 2.7259 | 143.0717
D.F.ZN00511/029878 | D.F.ZN00511/029878 | 0 | Maitland | RUTHERFORD |  | 380 | 3.9403 | 206.8143
D.F.ZN00511/029880 | D.F.ZN00511/029880 | 0 | Maitland | RUTHERFORD |  | 380 | 5.3544 | 281.0353 | 1
D.F.ZN00511/029881 | D.F.ZN00511/029881 | 0 | Maitland | RUTHERFORD |  | 380 | 3.2763 | 171.9612
D.F.ZN00511/029882 | D.F.ZN00511/029882 | 0 | Maitland | RUTHERFORD |  | 400 | 2.6503 | 139.1054
D.F.ZN00512/083733 | D.F.ZN00512/083733 | 0 | Singleton | BRANXTON |  | 400 | 3.3446 | 175.5464
D.F.ZN00512/083734 | D.F.ZN00512/083734 | 0 | Singleton | BRANXTON |  | 350 | 1.2076 | 63.3828
D.F.ZN00512/083736 | D.F.ZN00512/083736 | 0 | Singleton | BRANXTON |  | 400 | 4.4194 | 231.9605 | 1
D.F.ZN00512/083741 | D.F.ZN00512/083741 | 0 | Singleton | BRANXTON |  | 400 | 4.3556 | 228.609
D.F.ZN00512/083743 | D.F.ZN00512/083743 | 0 | Singleton | BRANXTON |  | 400 | 3.262 | 171.2082
D.F.ZN00513/083493 | D.F.ZN00513/083493 | 0 | Singleton | SINGLETON |  | 354 | 4.6272 | 242.8638
D.F.ZN00513/083495 | D.F.ZN00513/083495 | 0 | Singleton | SINGLETON |  | 400 | 3.8798 | 203.6359
D.F.ZN00513/083497 | D.F.ZN00513/083497 | 0 | Singleton | SINGLETON |  | 400 | 1.255 | 65.8717
D.F.ZN00513/083500 | D.F.ZN00513/083500 | 0 | Singleton | SINGLETON |  | 400 | 4.6474 | 243.9278 | 1
D.F.ZN00513/083502 | D.F.ZN00513/083502 | 0 | Singleton | SINGLETON |  | 400 | 2.0067 | 105.3218
D.F.ZN00513/083503 | D.F.ZN00513/083503 | 0 | Singleton | SINGLETON |  | 315 | 2.7532 | 144.5035
D.F.ZN00513/083504 | D.F.ZN00513/083504 | 0 | Singleton | SINGLETON |  | 320 | 3.1446 | 165.0478
D.F.ZN00514/018137 | D.F.ZN00514/018137 | 0 | Singleton | NEWDELL |  | 400 | 0.961 | 50.4374
D.F.ZN00514/018141 | D.F.ZN00514/018141 | 0 | Singleton | NEWDELL |  | 400 | 0.1976 | 10.3693
D.F.ZN00514/018156 | D.F.ZN00514/018156 | 0 | Singleton | NEWDELL |  | 290 | 1.7203 | 90.2916
D.F.ZN00514/018160 | D.F.ZN00514/018160 | 0 | Singleton | NEWDELL |  | 400 | 0.0129 | 0.6768
D.F.ZN00515/035192 | D.F.ZN00515/035192 | 0 | Singleton | MT THORLEY |  | 140 | 1.2785 | 67.1021
D.F.ZN00515/035193 | D.F.ZN00515/035193 | 0 | Singleton | MT THORLEY |  | 400 | 1.6294 | 85.5213
D.F.ZN00515/035197 | D.F.ZN00515/035197 | 0 | Singleton | MT THORLEY |  | 310 | 1.412 | 74.1108
D.F.ZN00515/035198 | D.F.ZN00515/035198 | 0 | Singleton | MT THORLEY |  | 400 | 1.1052 | 58.0082
D.F.ZN00515/035200 | D.F.ZN00515/035200 | 0 | Singleton | MT THORLEY |  | 400 | 2.6858 | 140.9676
D.F.ZN00516/048065 | D.F.ZN00516/048065 | 0 | Singleton | LEMINGTON |  | 220 | 0.9068 | 47.5934
D.F.ZN00516/048066 | D.F.ZN00516/048066 | 0 | Singleton | LEMINGTON |  | 335 | 0.6325 | 33.2002
D.F.ZN00516/048067 | D.F.ZN00516/048067 | 0 | Singleton | LEMINGTON |  | 400 | 1.6454 | 86.3624
D.F.ZN00520/048172 | D.F.ZN00520/048172 | 0 | #N/A | MITCHELLS FLAT |  | 132 | 1.6129 | 84.6559
D.F.ZN00522/083121 | D.F.ZN00522/083121 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 385 | 2.2763 | 119.4726
D.F.ZN00522/083123 | D.F.ZN00522/083123 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 335 | 5.2368 | 274.861 | 1
D.F.ZN00522/083124 | D.F.ZN00522/083124 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 400 | 5.2391 | 274.9829
D.F.ZN00522/083126 | D.F.ZN00522/083126 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 360 | 3.3629 | 176.5087
D.F.ZN00522/083129 | D.F.ZN00522/083129 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 305 | 3.8741 | 203.337 | 1
D.F.ZN00522/083130 | D.F.ZN00522/083130 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 385 | 2.2323 | 117.1634
D.F.ZN00522/083131 | D.F.ZN00522/083131 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 385 | 3.4594 | 181.5695
D.F.ZN00522/083132 | D.F.ZN00522/083132 | 0 | Greater Cessnock | CESSNOCK SOUTH |  | 335 | 2.3988 | 125.906
D.F.ZN00523/033500 | D.F.ZN00523/033500 | 0 | Singleton | SINGLETON NORTH |  | 400 | 0.793 | 41.6196
D.F.ZN00523/033501 | D.F.ZN00523/033501 | 0 | Singleton | SINGLETON NORTH |  | 400 | 3.3361 | 175.099
D.F.ZN00523/033503 | D.F.ZN00523/033503 | 0 | Singleton | SINGLETON NORTH |  | 320 | 2.3808 | 124.9595
D.F.ZN00523/033505 | D.F.ZN00523/033505 | 0 | Singleton | SINGLETON NORTH |  | 263 | 3.7044 | 194.4326
D.F.ZN00523/033507 | D.F.ZN00523/033507 | 0 | Singleton | SINGLETON NORTH |  | 384 | 2.11 | 110.7452
D.F.ZN00523/033508 | D.F.ZN00523/033508 | 0 | Singleton | SINGLETON NORTH |  | 400 | 2.6345 | 138.2731
D.F.ZN00523/033509 | D.F.ZN00523/033509 | 0 | Singleton | SINGLETON NORTH |  | 311 | 1.5961 | 83.7739
D.F.ZN00523/033511 | D.F.ZN00523/033511 | 0 | Singleton | SINGLETON NORTH |  | 383 | 1.1581 | 60.7832
D.F.ZN00524/033570 | D.F.ZN00524/033570 | 0 | Greater Cessnock | NULKABA |  | 400 | 3.7794 | 198.3664
D.F.ZN00524/033572 | D.F.ZN00524/033572 | 0 | Greater Cessnock | NULKABA |  | 400 | 4.8822 | 256.247
D.F.ZN00524/033574 | D.F.ZN00524/033574 | 0 | Greater Cessnock | NULKABA |  | 180 | 0.5365 | 28.1594
D.F.ZN00524/033576 | D.F.ZN00524/033576 | 0 | Greater Cessnock | NULKABA |  | 400 | 2.4544 | 128.8249
D.F.ZN00524/033578 | D.F.ZN00524/033578 | 0 | Greater Cessnock | NULKABA |  | 400 | 5.2852 | 277.4005 | 1
D.F.ZN00524/033580 | D.F.ZN00524/033580 | 0 | Greater Cessnock | NULKABA |  | 400 | 1.8644 | 97.8545
D.F.ZN00525/034580 | D.F.ZN00525/034580 | 0 | Greater Cessnock | TOMALPIN |  | 280 | 1.093 | 57.3655
D.F.ZN00525/034586 | D.F.ZN00525/034586 | 0 | Greater Cessnock | TOMALPIN |  | 400 | 0.0006 | 0.0323
D.F.ZN00525/034589 | D.F.ZN00525/034589 | 0 | Greater Cessnock | TOMALPIN |  | 400 | 1.9312 | 101.3617
D.F.ZN00526/034633 | D.F.ZN00526/034633 | 0 | Greater Cessnock | ROTHBURY |  | 400 | 0.9245 | 48.5237
D.F.ZN00526/034635 | D.F.ZN00526/034635 | 0 | Greater Cessnock | ROTHBURY |  | 120 | 0.1667 | 8.75
D.F.ZN00526/034636 | D.F.ZN00526/034636 | 0 | Greater Cessnock | ROTHBURY |  | 335 | 1.5984 | 83.8925
D.F.ZN00526/034637 | D.F.ZN00526/034637 | 0 | Greater Cessnock | ROTHBURY |  | 400 | 1.2961 | 68.0292
D.F.ZN00526/034639 | D.F.ZN00526/034639 | 0 | Greater Cessnock | ROTHBURY |  | 180 | 1.061 | 55.6906
D.F.ZN00526/034640 | D.F.ZN00526/034640 | 0 | Greater Cessnock | ROTHBURY |  | 330 | 3.6033 | 189.1258
D.F.ZN00526/034641 | D.F.ZN00526/034641 | 0 | Greater Cessnock | ROTHBURY |  | 335 | 5.2834 | 277.3075
D.F.ZN00526/034643 | D.F.ZN00526/034643 | 0 | Greater Cessnock | ROTHBURY |  | 400 | 2.5306 | 132.8233
D.F.ZN00526/034644 | D.F.ZN00526/034644 | 0 | Greater Cessnock | ROTHBURY |  | 400 | 0.2574 | 13.5122
D.F.ZN00528/083011 | D.F.ZN00528/083011 | 0 | Maitland | MAITLAND |  | 400 | 1.9769 | 103.7613 |  | CBZZN00528PA11 | 528:83020 | MAITLAND 33 | Maitland
D.F.ZN00528/083013 | D.F.ZN00528/083013 | 0 | Maitland | MAITLAND |  | 290 | 5.906 | 309.982 | 1 | CBZZN00528PA04 | 528:83019 | MAITLAND 33 | Maitland
D.F.ZN00528/083014 | D.F.ZN00528/083014 | 0 | Maitland | MAITLAND |  | 260 | 4.3121 | 226.3277 | 1 | CBZZN00528PA13 | 528:83014 | MAITLAND 33 | Maitland
D.F.ZN00528/083017 | D.F.ZN00528/083017 | 0 | Maitland | MAITLAND |  | 400 | 0.8662 | 45.4624 |  | CBZZN00528PA07 | 528:83013 | MAITLAND 33 | Maitland
D.F.ZN00528/083019 | D.F.ZN00528/083019 | 0 | Maitland | MAITLAND |  | 270 | 4.2307 | 222.0558 | 1
D.F.ZN00528/083020 | D.F.ZN00528/083020 | 0 | Maitland | MAITLAND |  | 260 | 4.8914 | 256.7324 | 1
D.F.ZN00528/083022 | D.F.ZN00528/083022 | 0 | Maitland | MAITLAND |  | 285 | 2.3738 | 124.5931
D.F.ZN00528/083024 | D.F.ZN00528/083024 | 0 | Maitland | MAITLAND |  | 385 | 3.2478 | 170.465
D.F.ZN00530/081060 | D.F.ZN00530/081060 | 0 | Singleton | HUNTER VALLEY CPP |  |  | 8.3992 | 440.8416
D.F.ZN00532/83291L | D.F.ZN00532/083291 | 0 | Maitland | METFORD |  | 400 | 1.3356 | 70.1004
D.F.ZN00532/083293 | D.F.ZN00532/083293 | 0 | Maitland | METFORD |  | 340 | 2.5933 | 136.1105
D.F.ZN00532/083295 | D.F.ZN00532/083295 | 0 | Maitland | METFORD |  | 280 | 3.6212 | 190.065
D.F.ZN00532/083298 | D.F.ZN00532/083298 | 0 | Maitland | METFORD |  | 400 | 4.9016 | 257.2668
D.F.ZN00532/083300 | D.F.ZN00532/083300 | 0 | Maitland | METFORD |  | 260 | 3.2528 | 170.7284
D.F.ZN00532/083301 | D.F.ZN00532/083301 | 0 | Maitland | METFORD |  | 400 | 7.5384 | 395.6618
D.F.ZN00532/083302 | D.F.ZN00532/083302 | 0 | Maitland | METFORD |  | 375 | 3.4493 | 181.0394
D.F.ZN00532/083304 | D.F.ZN00532/083304 | 0 | Maitland | METFORD |  | 400 | 0.7476 | 39.2404
D.F.ZN00532/083306 | D.F.ZN00532/083306 | 0 | Maitland | METFORD |  | 355 | 4.095 | 214.932
D.F.ZN00532/083307 | D.F.ZN00532/083307 | 0 | Maitland | METFORD |  | 315 | 3.4722 | 182.2449
D.F.ZN00532/083309 | D.F.ZN00532/083309 | 0 | Maitland | METFORD |  | 370 | 5.3657 | 281.6247
D.F.ZN00532/083312 | D.F.ZN00532/083312 | 0 | Maitland | METFORD |  | 359 | 2.0242 | 106.2442
D.F.ZN00532/083314 | D.F.ZN00532/083314 | 0 | Maitland | METFORD |  | 400 | 4.7969 | 251.7709
D.F.ZN00630/000004 | D.F.ZN00630/000004 | 0 | Eastern Suburbs Inner | MASCOT |  | 310 | 1.3772 | 72.2855
D.F.ZN00630/000010 | D.F.ZN00630/000010 | 0 | Eastern Suburbs Inner | MASCOT |  | 290 | 2.1237 | 111.4641
D.F.ZN00630/000016 | D.F.ZN00630/000016 | 0 | Eastern Suburbs Inner | MASCOT |  | 290 | 0.4396 | 23.0707
D.F.ZN00630/000018 | D.F.ZN00630/000018 | 0 | Eastern Suburbs Inner | MASCOT |  | 274 | 1.2295 | 64.5335
D.F.ZN00630/000019 | D.F.ZN00630/000019 | 0 | Eastern Suburbs Inner | MASCOT |  | 315 | 1.9395 | 101.7975
D.F.ZN00630/000022 | D.F.ZN00630/000022 | 0 | Eastern Suburbs Inner | MASCOT |  | 315 | 3.3419 | 175.4057
D.F.ZN00630/000023 | D.F.ZN00630/000023 | 0 | Eastern Suburbs Inner | MASCOT |  | 340 | 2.5752 | 135.1629
D.F.ZN00630/000024 | D.F.ZN00630/000024 | 0 | Eastern Suburbs Inner | MASCOT |  | 290 | 1.977 | 103.766
D.F.ZN00630/000025 | D.F.ZN00630/000025 | 0 | Eastern Suburbs Inner | MASCOT |  | 255 | 3.3176 | 174.1271
D.F.ZN00630/000027 | D.F.ZN00630/000027 | 0 | Eastern Suburbs Inner | MASCOT |  | 290 | 1.3943 | 73.1792
D.F.ZN00630/000030 | D.F.ZN00630/000030 | 0 | Eastern Suburbs Inner | MASCOT |  | 315 | 1.9488 | 102.2855
D.F.ZN00630/000031 | D.F.ZN00630/000031 | 0 | Eastern Suburbs Inner | MASCOT |  | 210 | 2.399 | 125.917
D.F.ZN00630/000032 | D.F.ZN00630/000032 | 0 | Eastern Suburbs Inner | MASCOT |  | 315 | 0.9148 | 48.0146
D.F.ZN00630/000033 | D.F.ZN00630/000033 | 0 | Eastern Suburbs Inner | MASCOT |  | 290 | 1.3458 | 70.6365
D.F.ZN00630/000034 | D.F.ZN00630/000034 | 0 | Eastern Suburbs Inner | MASCOT |  | 275 | 1.9174 | 100.6386
D.F.ZN00630/000035 | D.F.ZN00630/000035 | 0 | Eastern Suburbs Inner | MASCOT |  | 275 | 1.8046 | 94.7183
D.F.ZN00630/000038 | D.F.ZN00630/000038 | 0 | Eastern Suburbs Inner | MASCOT |  | 220 | 3.1528 | 165.4765
D.F.ZN00630/000040 | D.F.ZN00630/000040 | 0 | Eastern Suburbs Inner | MASCOT |  | 270 | 1.6225 | 85.1575
D.F.ZN00690/000001 | D.F.ZN00690/000001 | 0 | Canterbury Bankstown | CAMPSIE |  |  |  | 0
D.F.ZN00690/000003 | D.F.ZN00690/000003 | 0 | Canterbury Bankstown | CAMPSIE |  | 330 | 2.4326 | 127.6797
D.F.ZN00690/000004 | D.F.ZN00690/000004 | 0 | Canterbury Bankstown | CAMPSIE |  | 335 | 1.8019 | 94.577
D.F.ZN00690/000005 | D.F.ZN00690/000005 | 0 | Canterbury Bankstown | CAMPSIE |  | 320 | 2.3278 | 122.1767
D.F.ZN00690/000006 | D.F.ZN00690/000006 | 0 | Canterbury Bankstown | CAMPSIE |  | 330 | 2.7003 | 141.7279
D.F.ZN00690/000010 | D.F.ZN00690/000010 | 0 | Canterbury Bankstown | CAMPSIE |  | 220 | 2.2012 | 115.5315
D.F.ZN00690/000011 | D.F.ZN00690/000011 | 0 | Canterbury Bankstown | CAMPSIE |  | 305 | 3.8331 | 201.1844
D.F.ZN00690/000012 | D.F.ZN00690/000012 | 0 | Canterbury Bankstown | CAMPSIE |  | 330 | 3.4302 | 180.0371
D.F.ZN00690/000014 | D.F.ZN00690/000014 | 0 | Canterbury Bankstown | CAMPSIE |  | 365 | 3.199 | 167.9054
D.F.ZN00690/000015 | D.F.ZN00690/000015 | 0 | Canterbury Bankstown | CAMPSIE |  | 220 | 2.9214 | 153.3313
D.F.ZN00690/000016 | D.F.ZN00690/000016 | 0 | Canterbury Bankstown | CAMPSIE |  |  |  | 0
D.F.ZN00690/000017 | D.F.ZN00690/000017 | 0 | Canterbury Bankstown | CAMPSIE |  | 200 | 2.0357 | 106.8491
D.F.ZN00690/000018 | D.F.ZN00690/000018 | 0 | Canterbury Bankstown | CAMPSIE |  | 400 | 4.3134 | 226.3931
D.F.ZN00690/000023 | D.F.ZN00690/000023 | 0 | Canterbury Bankstown | CAMPSIE |  | 360 | 1.5109 | 79.2995
D.F.ZN00690/000024 | D.F.ZN00690/000024 | 0 | Canterbury Bankstown | CAMPSIE |  | 325 | 2.2951 | 120.4598
D.F.ZN00690/000025 | D.F.ZN00690/000025 | 0 | Canterbury Bankstown | CAMPSIE |  | 330 | 2.3057 | 121.0158
D.F.ZN00690/000026 | D.F.ZN00690/000026 | 0 | Canterbury Bankstown | CAMPSIE |  | 325 | 2.6209 | 137.5595
D.F.ZN00690/000027 | D.F.ZN00690/000027 | 0 | Canterbury Bankstown | CAMPSIE |  | 340 | 2.0346 | 106.7868
D.F.ZN00690/000028 | D.F.ZN00690/000028 | 0 | Canterbury Bankstown | CAMPSIE |  | 355 | 3.3821 | 177.5139
D.F.ZN00690/000029 | D.F.ZN00690/000029 | 0 | Canterbury Bankstown | CAMPSIE |  |  |  | 0
D.F.ZN00690/000030 | D.F.ZN00690/000030 | 0 | Canterbury Bankstown | CAMPSIE |  | 355 | 3.7029 | 194.3515
D.F.ZN00690/000033 | D.F.ZN00690/000033 | 0 | Canterbury Bankstown | CAMPSIE |  | 230 | 2.5933 | 136.1132
D.F.ZN00690/000034 | D.F.ZN00690/000034 | 0 | Canterbury Bankstown | CAMPSIE |  | 355 | 3.4488 | 181.0134
D.F.ZN00690/000035 | D.F.ZN00690/000035 | 0 | Canterbury Bankstown | CAMPSIE |  | 345 | 3.8303 | 201.0403
D.F.ZN00690/000036 | D.F.ZN00690/000036 | 0 | Canterbury Bankstown | CAMPSIE |  | 230 | 2.4457 | 128.3658
D.F.ZN00801/074117 | D.F.ZN00801/074117 | 0 | Upper Hunter | MUSWELLBROOK |  | 335 | 2.6707 | 140.1773
D.F.ZN00801/074118 | D.F.ZN00801/074118 | 0 | Upper Hunter | MUSWELLBROOK |  | 385 | 3.3858 | 177.7078
D.F.ZN00801/074119 | D.F.ZN00801/074119 | 0 | Upper Hunter | MUSWELLBROOK |  | 205 | 2.444 | 128.2749
D.F.ZN00801/074120 | D.F.ZN00801/074120 | 0 | Upper Hunter | MUSWELLBROOK |  | 385 | 2.0832 | 109.3382
D.F.ZN00801/074121 | D.F.ZN00801/074121 | 0 | Upper Hunter | MUSWELLBROOK |  | 277 | 1.4406 | 75.6114
D.F.ZN00801/074122 | D.F.ZN00801/074122 | 0 | Upper Hunter | MUSWELLBROOK |  | 380 | 4.2781 | 224.5416
D.F.ZN00801/074123 | D.F.ZN00801/074123 | 0 | Upper Hunter | MUSWELLBROOK |  | 335 | 1.0097 | 52.9945
D.F.ZN00802/082215 | D.F.ZN00802/082215 | 0 | Upper Hunter | BAERAMI |  | 180 | 0.1088 | 5.7116
D.F.ZN00802/082220 | D.F.ZN00802/082220 | 0 | Upper Hunter | BAERAMI |  | 74 | 0.1277 | 6.7001
D.F.ZN00802/082225 | D.F.ZN00802/082225 | 0 | Upper Hunter | BAERAMI |  | 74 | 0.3234 | 16.9762
D.F.ZN00806/082662 | D.F.ZN00806/082662 | 0 | Upper Hunter | MOONAN |  | 335 | 0.9101 | 47.7699
D.F.ZN00806/082667 | D.F.ZN00806/082667 | 0 | Upper Hunter | MOONAN |  | 111 | 0.0557 | 2.9217
D.F.ZN00807/074179 | D.F.ZN00807/074179 | 0 | Upper Hunter | DENMAN |  | 400 | 0.5841 | 30.6581
D.F.ZN00807/074180 | D.F.ZN00807/074180 | 0 | Upper Hunter | DENMAN |  | 379 | 0.3702 | 19.4286
D.F.ZN00807/074181 | D.F.ZN00807/074181 | 0 | Upper Hunter | DENMAN |  | 334 | 2.1939 | 115.1475
D.F.ZN00807/074183 | D.F.ZN00807/074183 | 0 | Upper Hunter | DENMAN |  | 335 | 0.8716 | 45.7458
D.F.ZN00807/074184 | D.F.ZN00807/074184 | 0 | Upper Hunter | DENMAN |  | 334 | 1.7656 | 92.6686
D.F.ZN00810/074050 | D.F.ZN00810/074050 | 0 | Upper Hunter | MERRIWA |  | 144 | 0.5746 | 30.1595
D.F.ZN00810/074054 | D.F.ZN00810/074054 | 0 | Upper Hunter | MERRIWA |  | 152 | 0.8037 | 42.1818
D.F.ZN00810/074058 | D.F.ZN00810/074058 | 0 | Upper Hunter | MERRIWA |  | 335 | 0.4811 | 25.2533
D.F.ZN00810/074062 | D.F.ZN00810/074062 | 0 | Upper Hunter | MERRIWA |  | 120 | 1.6017 | 84.069
D.F.ZN00811/074234 | D.F.ZN00811/074234 | 0 | Upper Hunter | ROUCHEL |  | 337 | 1.0256 | 53.8316
D.F.ZN00812/019065 | D.F.ZN00812/019065 | 0 | Upper Hunter | MITCHELL LINE |  | 328 | 1.992 | 104.5549
D.F.ZN00812/019066 | D.F.ZN00812/019066 | 0 | Upper Hunter | MITCHELL LINE |  | 400 | 3.7964 | 199.2602 | 1
D.F.ZN00812/019071 | D.F.ZN00812/019071 | 0 | Upper Hunter | MITCHELL LINE |  | 315 | 3.8642 | 202.816
D.F.ZN00812/019072 | D.F.ZN00812/019072 | 0 | Upper Hunter | MITCHELL LINE |  | 316 | 1.6519 | 86.7031
D.F.ZN00813/089055 | D.F.ZN00813/089055 | 0 | Upper Hunter | SCONE |  | 400 | 4.3563 | 228.6449
D.F.ZN00813/089058 | D.F.ZN00813/089058 | 0 | Upper Hunter | SCONE |  | 400 | 0.2209 | 11.5953
D.F.ZN00813/89059L | D.F.ZN00813/089059 | 0 | Upper Hunter | SCONE |  | 400 | 1.3412 | 70.3935
D.F.ZN00813/089061L | D.F.ZN00813/089061 | 0 | Upper Hunter | SCONE |  | 400 |  | 0
D.F.ZN00813/089062 | D.F.ZN00813/089062 | 0 | Upper Hunter | SCONE |  | 388 | 2.5938 | 136.1413
D.F.ZN00813/089063 | D.F.ZN00813/089063 | 0 | Upper Hunter | SCONE |  | 400 | 4.283 | 224.7975
D.F.ZN00813/089065 | D.F.ZN00813/089065 | 0 | Upper Hunter | SCONE |  | 400 | 2.3807 | 124.9547
D.F.ZN00814/082283 | D.F.ZN00814/082283 | 0 | Upper Hunter | ABERDEEN |  | 335 | 0.6104 | 32.0357
D.F.ZN00814/082285 | D.F.ZN00814/082285 | 0 | Upper Hunter | ABERDEEN |  | 335 | 0.4109 | 21.5649
D.F.ZN00814/082289 | D.F.ZN00814/082289 | 0 | Upper Hunter | ABERDEEN |  | 400 | 2.6942 | 141.4079
D.F.ZN00814/082291 | D.F.ZN00814/082291 | 0 | Upper Hunter | ABERDEEN |  | 335 | 1.8111 | 95.0582
D.F.ZN00847/000001 | D.F.ZN00847/000001 | 0 | North West Sydney | HORNSBY |  | 375 | 2.954 | 155.0468
D.F.ZN00847/000002 | D.F.ZN00847/000002 | 0 | North West Sydney | HORNSBY |  | 365 | 3.9139 | 205.4254
D.F.ZN00847/000005 | D.F.ZN00847/000005 | 0 | North West Sydney | HORNSBY |  | 320 | 4.1396 | 217.2721
D.F.ZN00847/000007 | D.F.ZN00847/000007 | 0 | North West Sydney | HORNSBY |  | 320 | 2.0762 | 108.9728
D.F.ZN00847/000010 | D.F.ZN00847/000010 | 0 | North West Sydney | HORNSBY |  | 300 | 3.6869 | 193.5111
D.F.ZN00847/000012 | D.F.ZN00847/000012 | 0 | North West Sydney | HORNSBY |  | 390 | 1.8999 | 99.7212
D.F.ZN00847/000014 | D.F.ZN00847/000014 | 0 | North West Sydney | HORNSBY |  | 325 | 1.3394 | 70.3004
D.F.ZN00847/000015 | D.F.ZN00847/000015 | 0 | North West Sydney | HORNSBY |  | 310 | 3.2337 | 169.723
D.F.ZN00847/000018 | D.F.ZN00847/000018 | 0 | North West Sydney | HORNSBY |  | 360 | 2.0925 | 109.8279
D.F.ZN00847/000019 | D.F.ZN00847/000019 | 0 | North West Sydney | HORNSBY |  | 335 | 3.1882 | 167.3391
D.F.ZN00847/000021 | D.F.ZN00847/000021 | 0 | North West Sydney | HORNSBY |  | 320 | 3.758 | 197.242
D.F.ZN00847/000022 | D.F.ZN00847/000022 | 0 | North West Sydney | HORNSBY |  | 330 | 3.4242 | 179.7214
D.F.ZN00847/000023 | D.F.ZN00847/000023 | 0 | North West Sydney | HORNSBY |  | 320 | 2.9639 | 155.5657
D.F.ZN00847/000026 | D.F.ZN00847/000026 | 0 | North West Sydney | HORNSBY |  | 285 | 0.1838 | 9.6453
D.F.ZN00847/000028 | D.F.ZN00847/000028 | 0 | North West Sydney | HORNSBY |  | 325 | 3.7338 | 195.9713
D.F.ZN00847/000029 | D.F.ZN00847/000029 | 0 | North West Sydney | HORNSBY |  | 330 | 4.4024 | 231.0638
D.F.ZN00847/000030 | D.F.ZN00847/000030 | 0 | North West Sydney | HORNSBY |  | 390 | 0.8466 | 44.4332
D.F.ZN00847/000031 | D.F.ZN00847/000031 | 0 | North West Sydney | HORNSBY |  | 400 | 3.9088 | 205.1566
D.F.ZN00847/000035 | D.F.ZN00847/000035 | 0 | North West Sydney | HORNSBY |  | 390 | 0.3634 | 19.0716
D.F.ZN00847/000036 | D.F.ZN00847/000036 | 0 | North West Sydney | HORNSBY |  | 360 | 3.6394 | 191.0193
D.F.ZN00847/000038 | D.F.ZN00847/000038 | 0 | North West Sydney | HORNSBY |  | 365 | 0.5775 | 30.3118
D.F.ZN00847/000039 | D.F.ZN00847/000039 | 0 | North West Sydney | HORNSBY |  | 325 | 3.7253 | 195.5279
D.F.ZN00847/000044 | D.F.ZN00847/000044 | 0 | North West Sydney | HORNSBY |  | 325 | 2.9701 | 155.8918
D.F.ZN00847/000045 | D.F.ZN00847/000045 | 0 | North West Sydney | HORNSBY |  | 390 | 1.7746 | 93.1404
D.F.ZN00847/000046 | D.F.ZN00847/000046 | 0 | North West Sydney | HORNSBY |  | 400 | 3.3655 | 176.644
D.F.ZN00847/000047 | D.F.ZN00847/000047 | 0 | North West Sydney | HORNSBY |  | 390 | 2.2672 | 118.9991
D.F.ZN00847/000048 | D.F.ZN00847/000048 | 0 | North West Sydney | HORNSBY |  | 325 | 1.447 | 75.9474
D.F.ZN00874/000002 | D.F.ZN00874/000002 | 0 | Inner West Sydney | CONCORD |  | 335 | 3.2484 | 170.4993
D.F.ZN00874/000003 | D.F.ZN00874/000003 | 0 | Inner West Sydney | CONCORD |  | 330 | 1.9547 | 102.5959
D.F.ZN00874/000004 | D.F.ZN00874/000004 | 0 | Inner West Sydney | CONCORD |  | 320 | 3.8732 | 203.2905 | 1
D.F.ZN00874/000007 | D.F.ZN00874/000007 | 0 | Inner West Sydney | CONCORD |  | 305 | 2.3811 | 124.9778
D.F.ZN00874/000008 | D.F.ZN00874/000008 | 0 | Inner West Sydney | CONCORD |  | 305 | 3.1639 | 166.0615
D.F.ZN00874/000009 | D.F.ZN00874/000009 | 0 | Inner West Sydney | CONCORD |  | 390 | 0.7901 | 41.471
D.F.ZN00874/000010 | D.F.ZN00874/000010 | 0 | Inner West Sydney | CONCORD |  | 400 | 3.6987 | 194.1306
D.F.ZN00874/000011 | D.F.ZN00874/000011 | 0 | Inner West Sydney | CONCORD |  | 310 | 3.089 | 162.1324
D.F.ZN00874/000012 | D.F.ZN00874/000012 | 0 | Inner West Sydney | CONCORD |  | 315 | 0.2382 | 12.5047
D.F.ZN00874/000015 | D.F.ZN00874/000015 | 0 | Inner West Sydney | CONCORD |  | 310 | 2.2522 | 118.208
D.F.ZN00874/000016 | D.F.ZN00874/000016 | 0 | Inner West Sydney | CONCORD |  | 315 | 2.7911 | 146.4951
D.F.ZN00874/000017 | D.F.ZN00874/000017 | 0 | Inner West Sydney | CONCORD |  | 305 | 3.4277 | 179.9089 | 1
D.F.ZN00874/000018 | D.F.ZN00874/000018 | 0 | Inner West Sydney | CONCORD |  | 305 | 3.5215 | 184.8318 | 1
D.F.ZN00874/000022 | D.F.ZN00874/000022 | 0 | Inner West Sydney | CONCORD |  | 280 | 3.3662 | 176.6775 | 1
D.F.ZN00874/000024 | D.F.ZN00874/000024 | 0 | Inner West Sydney | CONCORD |  | 365 | 1.0932 | 57.3799
D.F.ZN00874/000025 | D.F.ZN00874/000025 | 0 | Inner West Sydney | CONCORD |  | 330 | 1.0022 | 52.6018
D.F.ZN00874/000026 | D.F.ZN00874/000026 | 0 | Inner West Sydney | CONCORD |  | 240 | 0.8664 | 45.4733
D.F.ZN00901/000016 | D.F.ZN00901/000016 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 370 | 1.9574 | 102.7383
D.F.ZN00901/000017 | D.F.ZN00901/000017 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 400 | 1.9173 | 100.6344
D.F.ZN00901/000019 | D.F.ZN00901/000019 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 285 | 2.471 | 129.6921
D.F.ZN00901/000021 | D.F.ZN00901/000021 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 400 | 1.3722 | 72.0233
D.F.ZN00901/000022 | D.F.ZN00901/000022 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 400 | 2.0244 | 106.2544
D.F.ZN00901/000023 | D.F.ZN00901/000023 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 350 | 2.9048 | 152.4635
D.F.ZN00901/000026 | D.F.ZN00901/000026 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 400 | 5.1396 | 269.7589
D.F.ZN00901/000027 | D.F.ZN00901/000027 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 295 | 2.9076 | 152.6089
D.F.ZN00901/000029 | D.F.ZN00901/000029 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 400 | 1.5549 | 81.613
D.F.ZN00901/000031 | D.F.ZN00901/000031 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 400 | 3.4478 | 180.9614
D.F.ZN00901/000032 | D.F.ZN00901/000032 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 245 | 1.8359 | 96.3612
D.F.ZN00901/000036 | D.F.ZN00901/000036 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 275 | 2.3627 | 124.0073
D.F.ZN00901/000038 | D.F.ZN00901/000038 | 0 | Eastern Suburbs Inner | SURRY HILLS |  | 275 | 2.447 | 128.4319
D.F.ZN00931/000001 | D.F.ZN00931/000001 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 355 | 2.5847 | 135.6616
D.F.ZN00931/000002 | D.F.ZN00931/000002 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 400 | 3.4576 | 181.4778
D.F.ZN00931/000003 | D.F.ZN00931/000003 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 270 | 3.0406 | 159.5916
D.F.ZN00931/000004 | D.F.ZN00931/000004 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 280 | 1.3605 | 71.4079
D.F.ZN00931/000007 | D.F.ZN00931/000007 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 290 | 0.3935 | 20.6548
D.F.ZN00931/000008 | D.F.ZN00931/000008 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 350 | 2.1096 | 110.7266
D.F.ZN00931/000009 | D.F.ZN00931/000009 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 400 | 0.814 | 42.726
D.F.ZN00931/000010 | D.F.ZN00931/000010 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 400 | 3.2459 | 170.3633
D.F.ZN00931/000011 | D.F.ZN00931/000011 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 285 | 2.5401 | 133.3188
D.F.ZN00931/000012 | D.F.ZN00931/000012 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 310 | 1.7813 | 93.4939
D.F.ZN00931/00013L | D.F.ZN00931/000013 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 280 | 3.2275 | 169.4007
D.F.ZN00931/000014 | D.F.ZN00931/000014 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 280 | 0.5906 | 30.9963
D.F.ZN00931/00018L | D.F.ZN00931/000018 | 0 | Eastern Suburbs Inner | DARLINGHURST |  | 305 | 3.0214 | 158.5843
D.F.ZN00931/00018R | D.F.ZN00931/000018 | 1 | Eastern Suburbs Inner | DARLINGHURST |  | 330 | 0.7751 | 40.6825
D.F.ZN00965/000002 | D.F.ZN00965/000002 | 0 | North West Sydney | PENNANT HILLS |  | 320 | 1.3082 | 68.6609
D.F.ZN00965/000003 | D.F.ZN00965/000003 | 0 | North West Sydney | PENNANT HILLS |  | 380 | 4.2855 | 224.9322
D.F.ZN00965/000004 | D.F.ZN00965/000004 | 0 | North West Sydney | PENNANT HILLS |  | 320 | 3.5654 | 187.1327
D.F.ZN00965/000006 | D.F.ZN00965/000006 | 0 | North West Sydney | PENNANT HILLS |  | 340 | 2.91 | 152.7357
D.F.ZN00965/000008 | D.F.ZN00965/000008 | 0 | North West Sydney | PENNANT HILLS |  | 340 | 2.7143 | 142.4639
D.F.ZN00965/000013 | D.F.ZN00965/000013 | 0 | North West Sydney | PENNANT HILLS |  | 340 | 1.4503 | 76.1214
D.F.ZN00965/000015 | D.F.ZN00965/000015 | 0 | North West Sydney | PENNANT HILLS |  | 320 | 2.9167 | 153.0845
D.F.ZN00965/000016 | D.F.ZN00965/000016 | 0 | North West Sydney | PENNANT HILLS |  | 400 | 2.7868 | 146.2671
D.F.ZN00965/000017 | D.F.ZN00965/000017 | 0 | North West Sydney | PENNANT HILLS |  | 370 | 3.4166 | 179.3259
D.F.ZN00965/000020 | D.F.ZN00965/000020 | 0 | North West Sydney | PENNANT HILLS |  | 400 | 2.3604 | 123.8888
D.F.ZN00965/000021 | D.F.ZN00965/000021 | 0 | North West Sydney | PENNANT HILLS |  | 360 | 2.1113 | 110.8167
D.F.ZN00965/000022 | D.F.ZN00965/000022 | 0 | North West Sydney | PENNANT HILLS |  | 305 | 1.5183 | 79.6913
D.F.ZN00965/000024 | D.F.ZN00965/000024 | 0 | North West Sydney | PENNANT HILLS |  | 300 | 2.8299 | 148.5332
D.F.ZN00965/000026 | D.F.ZN00965/000026 | 0 | North West Sydney | PENNANT HILLS |  | 325 | 2.7585 | 144.7823
D.F.ZN00965/000028 | D.F.ZN00965/000028 | 0 | North West Sydney | PENNANT HILLS |  | 340 | 3.0337 | 159.226
D.F.ZN00965/000029 | D.F.ZN00965/000029 | 0 | North West Sydney | PENNANT HILLS |  | 385 | 1.9777 | 103.8041
D.F.ZN00965/000030 | D.F.ZN00965/000030 | 0 | North West Sydney | PENNANT HILLS |  | 390 | 3.4246 | 179.7473
D.F.ZN00965/000033 | D.F.ZN00965/000033 | 0 | North West Sydney | PENNANT HILLS |  | 400 | 2.0017 | 105.0606
D.F.ZN00965/000035 | D.F.ZN00965/000035 | 0 | North West Sydney | PENNANT HILLS |  | 325 | 2.7139 | 142.4419
D.F.ZN00965/000037 | D.F.ZN00965/000037 | 0 | North West Sydney | PENNANT HILLS |  | 385 | 3.1341 | 164.4988
D.F.ZN00965/000038 | D.F.ZN00965/000038 | 0 | North West Sydney | PENNANT HILLS |  | 320 | 2.9931 | 157.0987
D.F.ZN00965/000039 | D.F.ZN00965/000039 | 0 | North West Sydney | PENNANT HILLS |  | 390 | 1.2524 | 65.7315
D.F.ZN00965/000042 | D.F.ZN00965/000042 | 0 | North West Sydney | PENNANT HILLS |  | 345 | 3.0388 | 159.4977
D.F.ZN00965/000043 | D.F.ZN00965/000043 | 0 | North West Sydney | PENNANT HILLS |  | 340 | 3.2072 | 168.3342
D.F.ZN00965/000044 | D.F.ZN00965/000044 | 0 | North West Sydney | PENNANT HILLS |  | 315 | 1.0582 | 55.5422
D.F.ZN00965/000046 | D.F.ZN00965/000046 | 0 | North West Sydney | PENNANT HILLS |  | 325 | 2.959 | 155.3067
D.F.ZN00965/000047 | D.F.ZN00965/000047 | 0 | North West Sydney | PENNANT HILLS |  | 310 | 1.4074 | 73.8709
D.F.ZN01068/000015 | D.F.ZN01068/000015 | 0 | Inner West Sydney | LIDCOMBE | 1 | 300 | 1.0944 | 57.4405
D.F.ZN01068/000016 | D.F.ZN01068/000016 | 0 | Inner West Sydney | LIDCOMBE | 1 | 300 | 1.5923 | 83.5726
D.F.ZN01068/000017 | D.F.ZN01068/000017 | 0 | Inner West Sydney | LIDCOMBE | 1 | 300 | 2.1551 | 113.1134
D.F.ZN01068/000018 | D.F.ZN01068/000018 | 0 | Inner West Sydney | LIDCOMBE | 1 | 300 | 2.0353 | 106.8233
D.F.ZN01068/000019 | D.F.ZN01068/000019 | 0 | Inner West Sydney | LIDCOMBE |  | 380 | 2.1637 | 113.5659
D.F.ZN01068/000020 | D.F.ZN01068/000020 | 0 | Inner West Sydney | LIDCOMBE |  | 315 | 1.3357 | 70.1059
D.F.ZN01068/000021 | D.F.ZN01068/000021 | 0 | Inner West Sydney | LIDCOMBE |  | 400 | 1.8786 | 98.6013
D.F.ZN01068/000022 | D.F.ZN01068/000022 | 0 | Inner West Sydney | LIDCOMBE |  | 350 | 0.2764 | 14.5079
D.F.ZN01068/000026 | D.F.ZN01068/000026 | 0 | Inner West Sydney | LIDCOMBE |  | 315 | 2.3126 | 121.3815
D.F.ZN01068/000027 | D.F.ZN01068/000027 | 0 | Inner West Sydney | LIDCOMBE |  | 340 | 3.7733 | 198.0472
D.F.ZN01068/00028R | D.F.ZN01068/000028 | 0 | Inner West Sydney | LIDCOMBE |  | 400 | 0.8563 | 44.942
D.F.ZN01068/00028L | D.F.ZN01068/000028 | 1 | Inner West Sydney | LIDCOMBE |  | 320 | 0.8005 | 42.0168
D.F.ZN01068/000052 | D.F.ZN01068/000052 | 0 | Inner West Sydney | LIDCOMBE |  | 315 | 2.9147 | 152.982
D.F.ZN01068/000053 | D.F.ZN01068/000053 | 0 | Inner West Sydney | LIDCOMBE |  | 380 | 3.2418 | 170.1506
D.F.ZN01068/000054 | D.F.ZN01068/000054 | 0 | Inner West Sydney | LIDCOMBE |  | 230 | 1.7713 | 92.9712
D.F.ZN01068/000056 | D.F.ZN01068/000056 | 0 | Inner West Sydney | LIDCOMBE |  | 375 | 1.3801 | 72.4384
D.F.ZN01068/000057 | D.F.ZN01068/000057 | 0 | Inner West Sydney | LIDCOMBE |  | 385 |  | 0
D.F.ZN01068/000058 | D.F.ZN01068/000058 | 0 | Inner West Sydney | LIDCOMBE |  | 250 |  | 0
D.F.ZN01193/00010L | D.F.ZN01193/000010 | 0 | Upper North Shore | LINDFIELD |  | 350 | 2.9016 | 152.2935
D.F.ZN01193/000011 | D.F.ZN01193/000011 | 0 | Upper North Shore | LINDFIELD |  | 315 | 3.6304 | 190.5483
D.F.ZN01193/000012 | D.F.ZN01193/000012 | 0 | Upper North Shore | LINDFIELD |  | 330 | 3.4075 | 178.8465
D.F.ZN01193/000015 | D.F.ZN01193/000015 | 0 | Upper North Shore | LINDFIELD |  | 295 | 1.7416 | 91.4103
D.F.ZN01193/000016 | D.F.ZN01193/000016 | 0 | Upper North Shore | LINDFIELD |  | 305 | 2.4887 | 130.6237
D.F.ZN01193/000017 | D.F.ZN01193/000017 | 0 | Upper North Shore | LINDFIELD |  | 400 | 1.4044 | 73.7111
D.F.ZN01193/000020 | D.F.ZN01193/000020 | 0 | Upper North Shore | LINDFIELD |  | 305 | 0.2647 | 13.8921
D.F.ZN01193/000021 | D.F.ZN01193/000021 | 0 | Upper North Shore | LINDFIELD |  | 400 | 1.9832 | 104.0921
D.F.ZN01193/000022 | D.F.ZN01193/000022 | 0 | Upper North Shore | LINDFIELD |  | 295 | 2.4932 | 130.8575
D.F.ZN01193/000025 | D.F.ZN01193/000025 | 0 | Upper North Shore | LINDFIELD |  | 290 | 1.5149 | 79.512
D.F.ZN01193/000026 | D.F.ZN01193/000026 | 0 | Upper North Shore | LINDFIELD |  | 280 | 2.8983 | 152.1193
D.F.ZN01193/000027 | D.F.ZN01193/000027 | 0 | Upper North Shore | LINDFIELD |  | 290 | 2.7521 | 144.4504
D.F.ZN01193/00028L | D.F.ZN01193/000028 | 0 | Upper North Shore | LINDFIELD |  | 300 | 3.6453 | 191.3265
D.F.ZN01287/000002 | D.F.ZN01287/000002 | 0 | Canterbury Bankstown | REVESBY |  | 400 | 1.8734 | 98.3298
D.F.ZN01287/000003 | D.F.ZN01287/000003 | 0 | Canterbury Bankstown | REVESBY |  | 330 | 3.155 | 165.5924
D.F.ZN01287/000004 | D.F.ZN01287/000004 | 0 | Canterbury Bankstown | REVESBY |  | 310 | 2.615 | 137.2509
D.F.ZN01287/000005 | D.F.ZN01287/000005 | 0 | Canterbury Bankstown | REVESBY |  | 375 | 2.7218 | 142.8593
D.F.ZN01287/000006 | D.F.ZN01287/000006 | 0 | Canterbury Bankstown | REVESBY |  | 390 | 1.7594 | 92.3438
D.F.ZN01287/000011 | D.F.ZN01287/000011 | 0 | Canterbury Bankstown | REVESBY |  | 365 | 3.4449 | 180.8129
D.F.ZN01287/000012 | D.F.ZN01287/000012 | 0 | Canterbury Bankstown | REVESBY |  | 320 | 2.1366 | 112.1433
D.F.ZN01287/000015 | D.F.ZN01287/000015 | 0 | Canterbury Bankstown | REVESBY |  | 400 | 4.7044 | 246.9161
D.F.ZN01287/000016 | D.F.ZN01287/000016 | 0 | Canterbury Bankstown | REVESBY |  | 310 | 1.5809 | 82.9744
D.F.ZN01287/000017 | D.F.ZN01287/000017 | 0 | Canterbury Bankstown | REVESBY |  | 320 | 3.1026 | 162.8455
D.F.ZN01287/000018 | D.F.ZN01287/000018 | 0 | Canterbury Bankstown | REVESBY |  | 310 | 3.0557 | 160.381
D.F.ZN01287/000019 | D.F.ZN01287/000019 | 0 | Canterbury Bankstown | REVESBY |  | 400 | 3.1726 | 166.5158
D.F.ZN01287/000021 | D.F.ZN01287/000021 | 0 | Canterbury Bankstown | REVESBY |  | 295 | 3.762 | 197.4555
D.F.ZN01287/000022 | D.F.ZN01287/000022 | 0 | Canterbury Bankstown | REVESBY |  | 370 | 1.9079 | 100.1389
D.F.ZN01287/000023 | D.F.ZN01287/000023 | 0 | Canterbury Bankstown | REVESBY |  | 275 | 2.2799 | 119.6623
D.F.ZN01287/000024 | D.F.ZN01287/000024 | 0 | Canterbury Bankstown | REVESBY |  | 400 | 3.2661 | 171.4267
D.F.ZN01290/000002 | D.F.ZN01290/000002 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 400 | 2.9541 | 155.0511
D.F.ZN01290/000003 | D.F.ZN01290/000003 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 330 | 2.6479 | 138.9768
D.F.ZN01290/000008 | D.F.ZN01290/000008 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 310 | 2.7464 | 144.1497
D.F.ZN01290/000009 | D.F.ZN01290/000009 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 320 | 2.2344 | 117.2776
D.F.ZN01290/000010 | D.F.ZN01290/000010 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 320 | 0.82 | 43.0391
D.F.ZN01290/000011 | D.F.ZN01290/000011 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 307 | 3.203 | 168.1154
D.F.ZN01290/000012 | D.F.ZN01290/000012 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 307 | 4.3478 | 228.2017
D.F.ZN01290/000013 | D.F.ZN01290/000013 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 335 | 3.9245 | 205.9843
D.F.ZN01290/000016 | D.F.ZN01290/000016 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 350 | 0.3502 | 18.3808
D.F.ZN01290/000017 | D.F.ZN01290/000017 | 0 | Canterbury Bankstown | LEIGHTONFIELD |  | 395 | 1.6255 | 85.3177
D.F.ZN01610/000001 | D.F.ZN01610/000001 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.9177 | 100.6507
D.F.ZN01610/000002 | D.F.ZN01610/000002 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 340 | 2.0042 | 105.1926
D.F.ZN01610/000003 | D.F.ZN01610/000003 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.262 | 118.7267
D.F.ZN01610/000004 | D.F.ZN01610/000004 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.5825 | 135.5441
D.F.ZN01610/000005 | D.F.ZN01610/000005 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 310 | 2.9548 | 155.0886
D.F.ZN01610/000007 | D.F.ZN01610/000007 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.2774 | 67.0445
D.F.ZN01610/000008 | D.F.ZN01610/000008 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 3.306 | 173.5174
D.F.ZN01610/000010 | D.F.ZN01610/000010 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.1794 | 114.3909
D.F.ZN01610/000011 | D.F.ZN01610/000011 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.8039 | 147.1677
D.F.ZN01610/000012 | D.F.ZN01610/000012 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.1638 | 61.082
D.F.ZN01610/000013 | D.F.ZN01610/000013 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.1149 | 111.0015
D.F.ZN01610/000014 | D.F.ZN01610/000014 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.0484 | 107.5131
D.F.ZN01610/000016 | D.F.ZN01610/000016 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 4.4098 | 231.4559
D.F.ZN01610/000017 | D.F.ZN01610/000017 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.4497 | 128.5783
D.F.ZN01610/000018 | D.F.ZN01610/000018 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 2.3756 | 124.6842
D.F.ZN01610/000019 | D.F.ZN01610/000019 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 390 | 3.4432 | 180.7195
D.F.ZN01610/000020 | D.F.ZN01610/000020 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 350 | 3.0768 | 161.4885
D.F.ZN01610/000022 | D.F.ZN01610/000022 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 380 | 2.3694 | 124.3594
D.F.ZN01610/000023 | D.F.ZN01610/000023 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 3.0971 | 162.5574
D.F.ZN01610/000025 | D.F.ZN01610/000025 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.8927 | 99.3396
D.F.ZN01610/000026 | D.F.ZN01610/000026 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 340 | 2.4575 | 128.9873
D.F.ZN01610/000027 | D.F.ZN01610/000027 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.2918 | 67.8018
D.F.ZN01610/000028 | D.F.ZN01610/000028 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.998 | 104.8687
D.F.ZN01610/000029 | D.F.ZN01610/000029 | 0 | Inner West Sydney | HOMEBUSH BAY |  | 400 | 1.566 | 82.1944
D.F.ZN01673/00001L | D.F.ZN01673/000001 | 0 | Upper North Shore | TURRAMURRA |  | 355 | 3.711 | 194.7781
D.F.ZN01673/00001R | D.F.ZN01673/000001 | 1 | Upper North Shore | TURRAMURRA |  | 400 | 1.932 | 101.4052
D.F.ZN01673/000002 | D.F.ZN01673/000002 | 0 | Upper North Shore | TURRAMURRA |  | 315 | 2.2459 | 117.8781
D.F.ZN01673/000006 | D.F.ZN01673/000006 | 0 | Upper North Shore | TURRAMURRA |  | 315 | 2.8106 | 147.5159
D.F.ZN01673/000007 | D.F.ZN01673/000007 | 0 | Upper North Shore | TURRAMURRA |  | 385 | 3.2323 | 169.6506
D.F.ZN01673/000009 | D.F.ZN01673/000009 | 0 | Upper North Shore | TURRAMURRA |  | 400 | 2.6319 | 138.1411
D.F.ZN01673/00011L | D.F.ZN01673/000011 | 0 | Upper North Shore | TURRAMURRA |  | 400 | 1.495 | 78.4649
D.F.ZN01673/000013 | D.F.ZN01673/000013 | 0 | Upper North Shore | TURRAMURRA |  | 330 | 2.6732 | 140.3061
D.F.ZN01673/000014 | D.F.ZN01673/000014 | 0 | Upper North Shore | TURRAMURRA |  | 305 | 2.7179 | 142.6512
D.F.ZN01673/000018 | D.F.ZN01673/000018 | 0 | Upper North Shore | TURRAMURRA |  | 400 | 2.8844 | 151.3898
D.F.ZN01673/000019 | D.F.ZN01673/000019 | 0 | Upper North Shore | TURRAMURRA |  | 330 | 2.3204 | 121.7899
D.F.ZN01673/000020 | D.F.ZN01673/000020 | 0 | Upper North Shore | TURRAMURRA |  | 400 | 3.5615 | 186.9293
D.F.ZN01673/00021R | D.F.ZN01673/000021 | 0 | Upper North Shore | TURRAMURRA |  | 290 | 2.3911 | 125.5013
D.F.ZN01673/00021L | D.F.ZN01673/000021 | 1 | Upper North Shore | TURRAMURRA |  | 400 | 1.3434 | 70.5108
D.F.ZN01788/000014 | D.F.ZN01788/000014 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 315 | 2.3391 | 122.771
D.F.ZN01788/000015 | D.F.ZN01788/000015 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 3.2703 | 171.6486
D.F.ZN01788/000016 | D.F.ZN01788/000016 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 3.1183 | 163.666
D.F.ZN01788/000017 | D.F.ZN01788/000017 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 205 | 2.5997 | 136.4508
D.F.ZN01788/000042 | D.F.ZN01788/000042 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 395 | 1.8714 | 98.2225
D.F.ZN01788/000043 | D.F.ZN01788/000043 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 2.582 | 135.5219
D.F.ZN01788/000044 | D.F.ZN01788/000044 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 300 | 2.2551 | 118.362
D.F.ZN01788/000047 | D.F.ZN01788/000047 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 1.8802 | 98.684
D.F.ZN01788/000061 | D.F.ZN01788/000061 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 310 | 2.9858 | 156.7149
D.F.ZN01788/000062 | D.F.ZN01788/000062 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 290 | 0.4512 | 23.6819
D.F.ZN01788/000063 | D.F.ZN01788/000063 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 290 | 2.752 | 144.4425
D.F.ZN01788/000065 | D.F.ZN01788/000065 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 2.304 | 120.9286
D.F.ZN01788/000067 | D.F.ZN01788/000067 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 3.0373 | 159.416
D.F.ZN01788/000069 | D.F.ZN01788/000069 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 330 | 1.9849 | 104.1795
D.F.ZN01788/000070 | D.F.ZN01788/000070 | 0 | Eastern Suburbs Outer | MATRAVILLE |  | 400 | 1.9349 | 101.5559
D.F.ZN01850/000031 | D.F.ZN01850/000031 | 0 | Canterbury Bankstown | BASS HILL |  | 335 | 0.6172 | 32.3936
D.F.ZN01850/000032 | D.F.ZN01850/000032 | 0 | Canterbury Bankstown | BASS HILL |  | 400 | 2.6442 | 138.787
D.F.ZN01850/000033 | D.F.ZN01850/000033 | 0 | Canterbury Bankstown | BASS HILL |  | 325 | 3.1451 | 165.0733
D.F.ZN01850/000040 | D.F.ZN01850/000040 | 0 | Canterbury Bankstown | BASS HILL |  | 325 | 3.6268 | 190.3577
D.F.ZN01850/000041 | D.F.ZN01850/000041 | 0 | Canterbury Bankstown | BASS HILL |  | 325 | 2.9229 | 153.4136
D.F.ZN01850/000042 | D.F.ZN01850/000042 | 0 | Canterbury Bankstown | BASS HILL |  | 330 | 3.0439 | 159.7643
D.F.ZN01850/000044 | D.F.ZN01850/000044 | 0 | Canterbury Bankstown | BASS HILL |  | 400 | 0.4532 | 23.789
D.F.ZN01850/000045 | D.F.ZN01850/000045 | 0 | Canterbury Bankstown | BASS HILL |  | 400 | 1.4459 | 75.8919
D.F.ZN02196/000001 | D.F.ZN02196/000001 | 0 | Canterbury Bankstown | MILPERRA |  | 385 | 0.8263 | 43.37
D.F.ZN02196/000002 | D.F.ZN02196/000002 | 0 | Canterbury Bankstown | MILPERRA |  | 380 | 3.004 | 157.6704
D.F.ZN02196/000003 | D.F.ZN02196/000003 | 0 | Canterbury Bankstown | MILPERRA |  | 335 | 2.3752 | 124.6664
D.F.ZN02196/000004 | D.F.ZN02196/000004 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 1.5451 | 81.0978
D.F.ZN02196/000005 | D.F.ZN02196/000005 | 0 | Canterbury Bankstown | MILPERRA |  | 340 | 3.1883 | 167.3418
D.F.ZN02196/000006 | D.F.ZN02196/000006 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 1.8656 | 97.9177
D.F.ZN02196/000009 | D.F.ZN02196/000009 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 2.2406 | 117.6023
D.F.ZN02196/000010 | D.F.ZN02196/000010 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 1.8019 | 94.5757
D.F.ZN02196/000011 | D.F.ZN02196/000011 | 0 | Canterbury Bankstown | MILPERRA |  | 340 | 3.2408 | 170.0977
D.F.ZN02196/000012 | D.F.ZN02196/000012 | 0 | Canterbury Bankstown | MILPERRA |  | 400 |  | 0
D.F.ZN02196/000013 | D.F.ZN02196/000013 | 0 | Canterbury Bankstown | MILPERRA |  | 380 | 1.0762 | 56.4856
D.F.ZN02196/00014L | D.F.ZN02196/000014 | 0 | Canterbury Bankstown | MILPERRA |  | 380 | 3.0908 | 162.2235
D.F.ZN02196/00014R | D.F.ZN02196/000014 | 1 | Canterbury Bankstown | MILPERRA |  | 385 | 0.2276 | 11.9477
D.F.ZN02196/000017 | D.F.ZN02196/000017 | 0 | Canterbury Bankstown | MILPERRA |  | 340 | 3.5309 | 185.3223
D.F.ZN02196/000018 | D.F.ZN02196/000018 | 0 | Canterbury Bankstown | MILPERRA |  | 340 | 5.5181 | 289.6277
D.F.ZN02196/000019 | D.F.ZN02196/000019 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 2.4709 | 129.6865
D.F.ZN02196/000020 | D.F.ZN02196/000020 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 0.9578 | 50.2723
D.F.ZN02196/000021 | D.F.ZN02196/000021 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 2.6 | 136.4641
D.F.ZN02196/000022 | D.F.ZN02196/000022 | 0 | Canterbury Bankstown | MILPERRA |  | 340 | 1.8663 | 97.9579
D.F.ZN02196/000025 | D.F.ZN02196/000025 | 0 | Canterbury Bankstown | MILPERRA |  | 385 | 3.6782 | 193.0574
D.F.ZN02196/000026 | D.F.ZN02196/000026 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 3.8781 | 203.549
D.F.ZN02196/000027 | D.F.ZN02196/000027 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 1.0604 | 55.6566
D.F.ZN02196/000028 | D.F.ZN02196/000028 | 0 | Canterbury Bankstown | MILPERRA |  | 400 | 2.4884 | 130.6096
D.F.ZN02310/000002 | D.F.ZN02310/000002 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 250 | 0.8592 | 45.0975
D.F.ZN02310/000003 | D.F.ZN02310/000003 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 315 | 3.1114 | 163.304
D.F.ZN02310/000004 | D.F.ZN02310/000004 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 330 | 4.2353 | 222.2938
D.F.ZN02310/000008 | D.F.ZN02310/000008 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 400 | 2.3813 | 124.9834
D.F.ZN02310/000009 | D.F.ZN02310/000009 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 350 | 0.8283 | 43.4762
D.F.ZN02310/000010 | D.F.ZN02310/000010 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 330 | 3.28 | 172.1569
D.F.ZN02310/000014 | D.F.ZN02310/000014 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 315 | 3.4192 | 179.463
D.F.ZN02310/000015 | D.F.ZN02310/000015 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 385 | 2.7449 | 144.0691
D.F.ZN02310/000018 | D.F.ZN02310/000018 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 400 | 2.4021 | 126.0761
D.F.ZN02310/000019 | D.F.ZN02310/000019 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 350 | 3.0268 | 158.8676
D.F.ZN02310/000021 | D.F.ZN02310/000021 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 330 | 3.3321 | 174.8892
D.F.ZN02310/000023 | D.F.ZN02310/000023 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 380 | 3.2075 | 168.3486
D.F.ZN02310/000024 | D.F.ZN02310/000024 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 350 | 2.9128 | 152.88
D.F.ZN02310/000025 | D.F.ZN02310/000025 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 340 | 1.4417 | 75.6715
D.F.ZN02310/000028 | D.F.ZN02310/000028 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 400 |  | 0
D.F.ZN02310/000029 | D.F.ZN02310/000029 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 330 | 3.0831 | 161.8204
D.F.ZN02310/000030 | D.F.ZN02310/000030 | 0 | Canterbury Bankstown | PUNCHBOWL |  | 225 | 1.3328 | 69.9513
D.F.ZN02400/000011 | D.F.ZN02400/000011 | 0 | North West Sydney | BEROWRA |  | 350 | 1.631 | 85.6044 | 1
D.F.ZN02400/000013 | D.F.ZN02400/000013 | 0 | North West Sydney | BEROWRA |  | 380 | 1.2927 | 67.8515
D.F.ZN02400/000015 | D.F.ZN02400/000015 | 0 | North West Sydney | BEROWRA |  | 355 | 2.8966 | 152.0321
D.F.ZN02400/000018 | D.F.ZN02400/000018 | 0 | North West Sydney | BEROWRA |  | 320 | 3.4343 | 180.2533
D.F.ZN02400/000021 | D.F.ZN02400/000021 | 0 | North West Sydney | BEROWRA |  | 350 | 3.5928 | 188.5737 | 1
D.F.ZN02400/000022 | D.F.ZN02400/000022 | 0 | North West Sydney | BEROWRA |  | 320 | 3.1344 | 164.5124
D.F.ZN02400/000023 | D.F.ZN02400/000023 | 0 | North West Sydney | BEROWRA |  | 350 | 3.6893 | 193.6371
D.F.ZN02400/000026 | D.F.ZN02400/000026 | 0 | North West Sydney | BEROWRA |  | 350 | 2.2102 | 116.0035
D.F.ZN02466/000001 | D.F.ZN02466/000001 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 2.271 | 119.1954
D.F.ZN02466/000002 | D.F.ZN02466/000002 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 3.0306 | 159.0628
D.F.ZN02466/000003 | D.F.ZN02466/000003 | 0 | Inner West Sydney | FLEMINGTON |  | 385 | 3.2869 | 172.5165
D.F.ZN02466/000004 | D.F.ZN02466/000004 | 0 | Inner West Sydney | FLEMINGTON |  | 300 | 3.5301 | 185.2796
D.F.ZN02466/000005 | D.F.ZN02466/000005 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 2.1274 | 111.6598
D.F.ZN02466/000006 | D.F.ZN02466/000006 | 0 | Inner West Sydney | FLEMINGTON |  | 335 | 4.0452 | 212.3155
D.F.ZN02466/000007 | D.F.ZN02466/000007 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 3.4996 | 183.6828
D.F.ZN02466/000008 | D.F.ZN02466/000008 | 0 | Inner West Sydney | FLEMINGTON |  | 385 | 1.3752 | 72.1793
D.F.ZN02466/000011 | D.F.ZN02466/000011 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 2.4628 | 129.2629
D.F.ZN02466/000012 | D.F.ZN02466/000012 | 0 | Inner West Sydney | FLEMINGTON |  | 300 | 1.1165 | 58.6031
D.F.ZN02466/000015 | D.F.ZN02466/000015 | 0 | Inner West Sydney | FLEMINGTON |  | 310 | 1.3734 | 72.0863
D.F.ZN02466/000016 | D.F.ZN02466/000016 | 0 | Inner West Sydney | FLEMINGTON |  | 290 | 2.6847 | 140.9086
D.F.ZN02466/000017 | D.F.ZN02466/000017 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 0.3776 | 19.8189
D.F.ZN02466/000018 | D.F.ZN02466/000018 | 0 | Inner West Sydney | FLEMINGTON |  | 385 | 3.0261 | 158.8293
D.F.ZN02466/000019 | D.F.ZN02466/000019 | 0 | Inner West Sydney | FLEMINGTON |  | 340 | 0.5185 | 27.2117
D.F.ZN02466/000020 | D.F.ZN02466/000020 | 0 | Inner West Sydney | FLEMINGTON |  | 400 | 5.3563 | 281.1307
D.F.ZN02466/000021 | D.F.ZN02466/000021 | 0 | Inner West Sydney | FLEMINGTON |  | 315 | 5.5226 | 289.863
D.F.ZN02466/00022L | D.F.ZN02466/000022 | 0 | Inner West Sydney | FLEMINGTON |  | 385 | 4.3727 | 229.5097
D.F.ZN02466/00022R | D.F.ZN02466/000022 | 1 | Inner West Sydney | FLEMINGTON |  | 330 | 1.4249 | 74.7872
D.F.ZN02568/000006 | D.F.ZN02568/000006 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 390 | 3.6533 | 191.7477
D.F.ZN02568/000007 | D.F.ZN02568/000007 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 5.5272 | 290.1024
D.F.ZN02568/000008 | D.F.ZN02568/000008 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 390 | 5.1717 | 271.4441
D.F.ZN02568/000009 | D.F.ZN02568/000009 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 2.8825 | 151.2913
D.F.ZN02568/00014R | D.F.ZN02568/000014 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 4.3019 | 225.7897
D.F.ZN02568/00014L | D.F.ZN02568/000014 | 1 | Eastern Suburbs Inner | ST. PETERS |  | 320 | 1.7292 | 90.7595
D.F.ZN02568/000015 | D.F.ZN02568/000015 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 390 | 2.0458 | 107.3746
D.F.ZN02568/000016 | D.F.ZN02568/000016 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 2.1929 | 115.0961
D.F.ZN02568/000017 | D.F.ZN02568/000017 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 320 | 1.5472 | 81.2061
D.F.ZN02568/000018 | D.F.ZN02568/000018 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 3.5002 | 183.7116
D.F.ZN02568/000019 | D.F.ZN02568/000019 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 370 | 3.8439 | 201.7501
D.F.ZN02568/000020 | D.F.ZN02568/000020 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 4.0374 | 211.9111 | 1
D.F.ZN02568/000021 | D.F.ZN02568/000021 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 3.7195 | 195.2231
D.F.ZN02568/000022 | D.F.ZN02568/000022 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 320 | 1.3292 | 69.7627
D.F.ZN02568/000025 | D.F.ZN02568/000025 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 330 | 2.9197 | 153.2458
D.F.ZN02568/000026 | D.F.ZN02568/000026 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 368 | 4.342 | 227.895
D.F.ZN02568/000027 | D.F.ZN02568/000027 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 4.1434 | 217.4726
D.F.ZN02568/000028 | D.F.ZN02568/000028 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 2.7007 | 141.7495
D.F.ZN02568/000029 | D.F.ZN02568/000029 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 316 | 3.0985 | 162.6268
D.F.ZN02568/000030 | D.F.ZN02568/000030 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 230 |  | 0
D.F.ZN02568/000031 | D.F.ZN02568/000031 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 335 | 0.9704 | 50.9347
D.F.ZN02568/000032 | D.F.ZN02568/000032 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 316 | 3.7607 | 197.3864 | 1
D.F.ZN02568/000033 | D.F.ZN02568/000033 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 1.1908 | 62.4997
D.F.ZN02568/000038 | D.F.ZN02568/000038 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 230 | 3.218 | 168.9
D.F.ZN02568/000039 | D.F.ZN02568/000039 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 8.281 | 434.6403
D.F.ZN02568/000040 | D.F.ZN02568/000040 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 2.4092 | 126.4526
D.F.ZN02568/000041 | D.F.ZN02568/000041 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 390 | 4.0062 | 210.271
D.F.ZN02568/000042 | D.F.ZN02568/000042 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 1.4823 | 77.8012
D.F.ZN02568/000043 | D.F.ZN02568/000043 | 0 | Eastern Suburbs Inner | ST. PETERS |  | 400 | 0.4498 | 23.6074
D.F.ZN02602/000027 | D.F.ZN02602/000027 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 400 | 4.9022 | 257.2979
D.F.ZN02602/000028 | D.F.ZN02602/000028 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 305 | 3.046 | 159.8741
D.F.ZN02602/000029 | D.F.ZN02602/000029 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 400 | 2.4209 | 127.0643
D.F.ZN02602/000030 | D.F.ZN02602/000030 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 400 | 4.2248 | 221.7421
D.F.ZN02602/000031 | D.F.ZN02602/000031 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 400 | 4.0143 | 210.695
D.F.ZN02602/000032 | D.F.ZN02602/000032 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 400 | 3.9718 | 208.4631
D.F.ZN02602/000033 | D.F.ZN02602/000033 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 365 | 1.7113 | 89.8173
D.F.ZN02602/000034 | D.F.ZN02602/000034 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 195 | 2.6031 | 136.6259
D.F.ZN02602/000035 | D.F.ZN02602/000035 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 400 | 4.4071 | 231.3104
D.F.ZN02602/000036 | D.F.ZN02602/000036 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 370 | 3.3866 | 177.7517
D.F.ZN02602/000041 | D.F.ZN02602/000041 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 370 | 2.1405 | 112.3484
D.F.ZN02602/000042 | D.F.ZN02602/000042 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 335 | 4.4373 | 232.8976
D.F.ZN02602/000046 | D.F.ZN02602/000046 | 0 | Eastern Suburbs Outer | CLOVELLY |  | 385 | 2.0596 | 108.0995
D.F.ZN02635/000031 | D.F.ZN02635/000031 | 0 | Carlingford | EPPING |  | 305 | 1.8354 | 96.3356
D.F.ZN02635/000032 | D.F.ZN02635/000032 | 0 | Carlingford | EPPING |  | 295 | 2.3714 | 124.4655
D.F.ZN02635/000033 | D.F.ZN02635/000033 | 0 | Carlingford | EPPING |  | 365 | 4.2299 | 222.0131
D.F.ZN02635/000035 | D.F.ZN02635/000035 | 0 | Carlingford | EPPING |  | 310 | 3.616 | 189.7917
D.F.ZN02635/000036 | D.F.ZN02635/000036 | 0 | Carlingford | EPPING |  | 400 | 0.7738 | 40.615
D.F.ZN02635/000038 | D.F.ZN02635/000038 | 0 | Carlingford | EPPING |  | 315 | 2.4496 | 128.5713
D.F.ZN02635/000039 | D.F.ZN02635/000039 | 0 | Carlingford | EPPING |  | 395 | 1.9486 | 102.2739
D.F.ZN02635/000040 | D.F.ZN02635/000040 | 0 | Carlingford | EPPING |  | 370 | 2.9853 | 156.6886
D.F.ZN02635/000041 | D.F.ZN02635/000041 | 0 | Carlingford | EPPING |  | 395 | 2.6361 | 138.3583
D.F.ZN02635/000043 | D.F.ZN02635/000043 | 0 | Carlingford | EPPING |  | 395 | 2.6699 | 140.1322
D.F.ZN02635/000044 | D.F.ZN02635/000044 | 0 | Carlingford | EPPING |  | 350 | 1.8113 | 95.0695
D.F.ZN02635/000046 | D.F.ZN02635/000046 | 0 | Carlingford | EPPING |  | 370 | 2.6365 | 138.3787
D.F.ZN02635/000047 | D.F.ZN02635/000047 | 0 | Carlingford | EPPING |  | 310 | 3.3517 | 175.9205
D.F.ZN02635/000048 | D.F.ZN02635/000048 | 0 | Carlingford | EPPING |  | 400 |  | 0
D.F.ZN02635/000050 | D.F.ZN02635/000050 | 0 | Carlingford | EPPING |  | 400 | 2.5222 | 132.3837
D.F.ZN02635/000051 | D.F.ZN02635/000051 | 0 | Carlingford | EPPING |  | 395 | 2.6536 | 139.2762
D.F.ZN02635/000052 | D.F.ZN02635/000052 | 0 | Carlingford | EPPING |  | 280 | 3.1328 | 164.4285
D.F.ZN02635/000053 | D.F.ZN02635/000053 | 0 | Carlingford | EPPING |  | 400 | 1.9903 | 104.4622
D.F.ZN02635/000055 | D.F.ZN02635/000055 | 0 | Carlingford | EPPING |  | 315 | 3.6082 | 189.3789
D.F.ZN02635/000057 | D.F.ZN02635/000057 | 0 | Carlingford | EPPING |  | 295 | 1.9969 | 104.8109
D.F.ZN02635/000058 | D.F.ZN02635/000058 | 0 | Carlingford | EPPING |  | 395 | 3.8273 | 200.8834
D.F.ZN02635/000059 | D.F.ZN02635/000059 | 0 | Carlingford | EPPING |  | 400 | 2.0644 | 108.3538
D.F.ZN02635/000060 | D.F.ZN02635/000060 | 0 | Carlingford | EPPING |  | 400 |  | 0
D.F.ZN02635/000062 | D.F.ZN02635/000062 | 0 | Carlingford | EPPING |  | 400 | 3.132 | 164.3885
D.F.ZN02635/000064 | D.F.ZN02635/000064 | 0 | Carlingford | EPPING |  | 365 | 2.3594 | 123.8366
D.F.ZN02635/000065 | D.F.ZN02635/000065 | 0 | Carlingford | EPPING |  | 305 | 2.1333 | 111.9714
D.F.ZN02835/000007 | D.F.ZN02835/000007 | 0 | Inner West Sydney | BURWOOD |  | 400 | 2.0177 | 105.9042
D.F.ZN02835/000008 | D.F.ZN02835/000008 | 0 | Inner West Sydney | BURWOOD |  | 400 | 2.2625 | 118.7526
D.F.ZN02835/000009 | D.F.ZN02835/000009 | 0 | Inner West Sydney | BURWOOD |  | 390 | 5.065 | 265.845 | 1
D.F.ZN02835/000010 | D.F.ZN02835/000010 | 0 | Inner West Sydney | BURWOOD |  | 400 | 2.923 | 153.4188
D.F.ZN02835/000015 | D.F.ZN02835/000015 | 0 | Inner West Sydney | BURWOOD |  | 300 | 2.538 | 133.2114
D.F.ZN02835/000016 | D.F.ZN02835/000016 | 0 | Inner West Sydney | BURWOOD |  | 375 | 4.7962 | 251.7364
D.F.ZN02835/000017 | D.F.ZN02835/000017 | 0 | Inner West Sydney | BURWOOD |  | 325 | 2.4307 | 127.5808
D.F.ZN02835/000018 | D.F.ZN02835/000018 | 0 | Inner West Sydney | BURWOOD |  | 220 | 1.228 | 64.4536
D.F.ZN02835/000019 | D.F.ZN02835/000019 | 0 | Inner West Sydney | BURWOOD |  | 400 | 3.0033 | 157.6325 | 1
D.F.ZN02835/000020 | D.F.ZN02835/000020 | 0 | Inner West Sydney | BURWOOD |  | 340 | 2.0778 | 109.0558
D.F.ZN02835/000021 | D.F.ZN02835/000021 | 0 | Inner West Sydney | BURWOOD |  | 400 | 3.6735 | 192.8101
D.F.ZN02835/000022 | D.F.ZN02835/000022 | 0 | Inner West Sydney | BURWOOD |  | 400 | 1.3097 | 68.7393
D.F.ZN02835/00023L | D.F.ZN02835/000023 | 0 | Inner West Sydney | BURWOOD |  | 350 | 1.634 | 85.763
D.F.ZN02835/000024 | D.F.ZN02835/000024 | 0 | Inner West Sydney | BURWOOD |  | 300 | 2.2841 | 119.884
D.F.ZN02835/000027 | D.F.ZN02835/000027 | 0 | Inner West Sydney | BURWOOD |  | 330 | 2.4659 | 129.4286
D.F.ZN02835/000028 | D.F.ZN02835/000028 | 0 | Inner West Sydney | BURWOOD |  | 220 | 2.5899 | 135.935
D.F.ZN02835/000029 | D.F.ZN02835/000029 | 0 | Inner West Sydney | BURWOOD |  | 220 | 1.5165 | 79.5979
D.F.ZN02835/000030 | D.F.ZN02835/000030 | 0 | Inner West Sydney | BURWOOD |  | 400 | 3.0798 | 161.6471
D.F.ZN02835/000031 | D.F.ZN02835/000031 | 0 | Inner West Sydney | BURWOOD |  | 400 | 4.5873 | 240.7716
D.F.ZN02835/000032 | D.F.ZN02835/000032 | 0 | Inner West Sydney | BURWOOD |  | 220 | 1.836 | 96.365
D.F.ZN02835/000033 | D.F.ZN02835/000033 | 0 | Inner West Sydney | BURWOOD |  | 290 | 2.2615 | 118.6958
D.F.ZN02835/000034 | D.F.ZN02835/000034 | 0 | Inner West Sydney | BURWOOD |  | 400 | 3.6782 | 193.0539
D.F.ZN02835/000035 | D.F.ZN02835/000035 | 0 | Inner West Sydney | BURWOOD |  | 305 | 2.0223 | 106.1442
D.F.ZN02835/000036 | D.F.ZN02835/000036 | 0 | Inner West Sydney | BURWOOD |  | 320 | 2.5854 | 135.6957
D.F.ZN02835/000041 | D.F.ZN02835/000041 | 0 | Inner West Sydney | BURWOOD |  | 330 | 2.5967 | 136.2911
D.F.ZN02835/000042 | D.F.ZN02835/000042 | 0 | Inner West Sydney | BURWOOD |  | 325 | 1.0473 | 54.9711
D.F.ZN02835/000043 | D.F.ZN02835/000043 | 0 | Inner West Sydney | BURWOOD |  | 330 | 4.0529 | 212.7201
D.F.ZN03154/000003 | D.F.ZN03154/000003 | 0 | Upper North Shore | ST. IVES |  | 345 | 1.1663 | 61.2147
D.F.ZN03154/000004 | D.F.ZN03154/000004 | 0 | Upper North Shore | ST. IVES |  | 400 | 3.3353 | 175.0578
D.F.ZN03154/000005 | D.F.ZN03154/000005 | 0 | Upper North Shore | ST. IVES |  | 350 | 2.5496 | 133.8209
D.F.ZN03154/000006 | D.F.ZN03154/000006 | 0 | Upper North Shore | ST. IVES |  | 400 | 1.7611 | 92.4317
D.F.ZN03154/000010 | D.F.ZN03154/000010 | 0 | Upper North Shore | ST. IVES |  | 380 | 2.8084 | 147.4039
D.F.ZN03154/000011 | D.F.ZN03154/000011 | 0 | Upper North Shore | ST. IVES |  | 335 | 2.6213 | 137.5802
D.F.ZN03154/000012 | D.F.ZN03154/000012 | 0 | Upper North Shore | ST. IVES |  | 345 | 2.6653 | 139.8902
D.F.ZN03154/000013 | D.F.ZN03154/000013 | 0 | Upper North Shore | ST. IVES |  | 320 | 1.8586 | 97.5515
D.F.ZN03154/000014 | D.F.ZN03154/000014 | 0 | Upper North Shore | ST. IVES |  | 400 | 1.2485 | 65.5305
D.F.ZN03154/000016 | D.F.ZN03154/000016 | 0 | Upper North Shore | ST. IVES |  | 340 | 2.7954 | 146.7191
D.F.ZN03154/000017 | D.F.ZN03154/000017 | 0 | Upper North Shore | ST. IVES |  | 400 | 2.4005 | 125.9948
D.F.ZN03154/000018 | D.F.ZN03154/000018 | 0 | Upper North Shore | ST. IVES |  | 385 | 3.5132 | 184.3957
D.F.ZN03154/000019 | D.F.ZN03154/000019 | 0 | Upper North Shore | ST. IVES |  | 345 | 2.8249 | 148.2712
D.F.ZN03154/000022 | D.F.ZN03154/000022 | 0 | Upper North Shore | ST. IVES |  | 345 | 2.1966 | 115.2909
D.F.ZN03154/000023 | D.F.ZN03154/000023 | 0 | Upper North Shore | ST. IVES |  | 400 | 1.8791 | 98.6292
D.F.ZN03154/000024 | D.F.ZN03154/000024 | 0 | Upper North Shore | ST. IVES |  | 400 | 2.6935 | 141.3722
D.F.ZN03154/000025 | D.F.ZN03154/000025 | 0 | Upper North Shore | ST. IVES |  | 400 | 1.3619 | 71.4837
D.F.ZN03155/000011 | D.F.ZN03155/000011 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 295 | 3.0249 | 158.766
D.F.ZN03155/000012 | D.F.ZN03155/000012 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 305 | 2.304 | 120.9287
D.F.ZN03155/000015 | D.F.ZN03155/000015 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 305 | 2.5927 | 136.0801
D.F.ZN03155/000016 | D.F.ZN03155/000016 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 400 | 2.5356 | 133.0828
D.F.ZN03155/00017L | D.F.ZN03155/000017 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 215 | 1.3688 | 71.8434
D.F.ZN03155/000018 | D.F.ZN03155/000018 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 400 | 1.7717 | 92.9913
D.F.ZN03155/000019 | D.F.ZN03155/000019 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 315 | 3.1003 | 162.7227
D.F.ZN03155/000020 | D.F.ZN03155/000020 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 310 | 2.2904 | 120.2134
D.F.ZN03155/000021 | D.F.ZN03155/000021 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 270 | 1.5768 | 82.7585
D.F.ZN03155/000022 | D.F.ZN03155/000022 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 330 | 2.6546 | 139.3279
D.F.ZN03155/00023R | D.F.ZN03155/000023 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 205 | 1.7345 | 91.0385
D.F.ZN03155/000024 | D.F.ZN03155/000024 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 325 | 4.8435 | 254.2169
D.F.ZN03155/000027 | D.F.ZN03155/000027 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 400 | 5.2318 | 274.5983
D.F.ZN03155/000028 | D.F.ZN03155/000028 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 380 | 1.1041 | 57.9502
D.F.ZN03155/000029 | D.F.ZN03155/000029 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 365 | 3.3504 | 175.8509
D.F.ZN03155/000030 | D.F.ZN03155/000030 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 380 | 3.13 | 164.2804
D.F.ZN03155/000031 | D.F.ZN03155/000031 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 380 | 0.1752 | 9.1939
D.F.ZN03155/000032 | D.F.ZN03155/000032 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 325 | 1.7456 | 91.6205
D.F.ZN03155/000033 | D.F.ZN03155/000033 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 365 | 2.6383 | 138.474
D.F.ZN03155/000034 | D.F.ZN03155/000034 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 365 | 2.2551 | 118.3596
D.F.ZN03155/000035 | D.F.ZN03155/000035 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 370 | 2.5248 | 132.5159
D.F.ZN03155/000036 | D.F.ZN03155/000036 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 315 | 1.4167 | 74.3586
D.F.ZN03155/000039 | D.F.ZN03155/000039 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 300 | 1.578 | 82.8253
D.F.ZN03155/000040 | D.F.ZN03155/000040 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 310 | 3.594 | 188.6381
D.F.ZN03155/000044 | D.F.ZN03155/000044 | 0 | Eastern Suburbs Outer | DOUBLE BAY |  | 365 | 4.1408 | 217.3354
D.F.ZN03288/00041L | D.F.ZN03288/000041 | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 4.2662 | 223.9151
D.F.ZN03288/00042L | D.F.ZN03288/000042 | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.3956 | 73.2494
D.F.ZN03288/00043L | D.F.ZN03288/000043 | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.7661 | 92.6961
D.F.ZN03288/00044L | D.F.ZN03288/000044 | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.9407 | 49.3722
D.F.ZN03288/00045L | D.F.ZN03288/000045 | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 4.5945 | 241.1474
D.F.ZN03288/00046L | D.F.ZN03288/000046 | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.8372 | 43.9408
D.F.ZN03288/00041A | D.F.ZN03288/00041A | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.2351 | 64.8272
D.F.ZN03288/00041B | D.F.ZN03288/00041B | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.1108 | 58.3009
D.F.ZN03288/00041C | D.F.ZN03288/00041C | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.0528 | 2.7713
D.F.ZN03288/00041D | D.F.ZN03288/00041D | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.4753 | 24.9482
D.F.ZN03288/00041E | D.F.ZN03288/00041E | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.924 | 100.9817
D.F.ZN03288/00041F | D.F.ZN03288/00041F | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.3036 | 120.9058
D.F.ZN03288/00041G | D.F.ZN03288/00041G | 0 | Sydney CBD | CITY SOUTH |  |  |  | 0
D.F.ZN03288/00041J | D.F.ZN03288/00041J | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.191 | 115.0001
D.F.ZN03288/00041K | D.F.ZN03288/00041K | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.5259 | 80.0908
D.F.ZN03288/00041M | D.F.ZN03288/00041M | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.2122 | 63.624
D.F.ZN03288/00042A | D.F.ZN03288/00042A | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 3.0419 | 159.6573
D.F.ZN03288/00042C | D.F.ZN03288/00042C | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.3666 | 19.2418
D.F.ZN03288/00042D | D.F.ZN03288/00042D | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 4.5785 | 240.3099
D.F.ZN03288/00042E | D.F.ZN03288/00042E | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.4718 | 24.7632
D.F.ZN03288/00042F | D.F.ZN03288/00042F | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.6649 | 34.8962
D.F.ZN03288/00042G | D.F.ZN03288/00042G | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.3991 | 73.4321
D.F.ZN03288/00042H | D.F.ZN03288/00042H | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.8795 | 46.1601
D.F.ZN03288/00042J | D.F.ZN03288/00042J | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.9327 | 153.9245
D.F.ZN03288/00042K | D.F.ZN03288/00042K | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.1451 | 112.5895
D.F.ZN03288/00042M | D.F.ZN03288/00042M | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.4539 | 76.3111
D.F.ZN03288/00043A | D.F.ZN03288/00043A | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.6792 | 88.1354
D.F.ZN03288/00043B | D.F.ZN03288/00043B | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.4807 | 25.2302
D.F.ZN03288/00043C | D.F.ZN03288/00043C | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.6825 | 140.7964
D.F.ZN03288/00043D | D.F.ZN03288/00043D | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 4.0855 | 214.4322
D.F.ZN03288/00043F | D.F.ZN03288/00043F | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.9513 | 49.9297
D.F.ZN03288/00043G | D.F.ZN03288/00043G | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 3.7587 | 197.2786
D.F.ZN03288/00043H | D.F.ZN03288/00043H | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.7483 | 39.2738
D.F.ZN03288/00043J | D.F.ZN03288/00043J | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.9501 | 102.3543
D.F.ZN03288/00043K | D.F.ZN03288/00043K | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.9102 | 100.2573
D.F.ZN03288/00043M | D.F.ZN03288/00043M | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.1549 | 8.128
D.F.ZN03288/00044A | D.F.ZN03288/00044A | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.9315 | 101.3792
D.F.ZN03288/00044B | D.F.ZN03288/00044B | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.6156 | 32.3089
D.F.ZN03288/00044C | D.F.ZN03288/00044C | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.2848 | 119.9222
D.F.ZN03288/00044G | D.F.ZN03288/00044G | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 3.1956 | 167.7246
D.F.ZN03288/00044J | D.F.ZN03288/00044J | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.8072 | 94.8541
D.F.ZN03288/00044K | D.F.ZN03288/00044K | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.9117 | 100.3381
D.F.ZN03288/00044M | D.F.ZN03288/00044M | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.2439 | 117.7762
D.F.ZN03288/00045A | D.F.ZN03288/00045A | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.0794 | 109.1391
D.F.ZN03288/00045B | D.F.ZN03288/00045B | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.8372 | 148.9122
D.F.ZN03288/00045D | D.F.ZN03288/00045D | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.2413 | 117.6374
D.F.ZN03288/00045E | D.F.ZN03288/00045E | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 3.1168 | 163.5918
D.F.ZN03288/00045F | D.F.ZN03288/00045F | 0 | Sydney CBD | CITY SOUTH |  |  |  | 0
D.F.ZN03288/00045G | D.F.ZN03288/00045G | 0 | Sydney CBD | CITY SOUTH |  |  |  | 0
D.F.ZN03288/00045H | D.F.ZN03288/00045H | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.0736 | 56.3514
D.F.ZN03288/00045K | D.F.ZN03288/00045K | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 3.1611 | 165.9143
D.F.ZN03288/00045M | D.F.ZN03288/00045M | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.0316 | 1.6593
D.F.ZN03288/00046A | D.F.ZN03288/00046A | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.1977 | 10.3784
D.F.ZN03288/00046B | D.F.ZN03288/00046B | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.32 | 121.7705
D.F.ZN03288/00046C | D.F.ZN03288/00046C | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 2.6944 | 141.4198
D.F.ZN03288/00046D | D.F.ZN03288/00046D | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.3787 | 72.3646
D.F.ZN03288/00046E | D.F.ZN03288/00046E | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.3566 | 71.2051
D.F.ZN03288/00046F | D.F.ZN03288/00046F | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 3.9095 | 205.1935
D.F.ZN03288/00046G | D.F.ZN03288/00046G | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.6053 | 84.2578
D.F.ZN03288/00046H | D.F.ZN03288/00046H | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 1.4407 | 75.6183
D.F.ZN03288/00046J | D.F.ZN03288/00046J | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.3656 | 19.1902
D.F.ZN03288/00046K | D.F.ZN03288/00046K | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 0.1707 | 8.9596
D.F.ZN03288/00046M | D.F.ZN03288/00046M | 0 | Sydney CBD | CITY SOUTH | 1 | 300 | 4.0676 | 213.491
D.F.ZN03425/000007 | D.F.ZN03425/000007 | 0 | Lower North Shore | CASTLE COVE |  | 370 | 1.7125 | 89.8855
D.F.ZN03425/000008 | D.F.ZN03425/000008 | 0 | Lower North Shore | CASTLE COVE |  | 315 | 3.8084 | 199.8868
D.F.ZN03425/000011 | D.F.ZN03425/000011 | 0 | Lower North Shore | CASTLE COVE |  | 295 | 3.3341 | 174.9937
D.F.ZN03425/000012 | D.F.ZN03425/000012 | 0 | Lower North Shore | CASTLE COVE |  | 315 | 2.0765 | 108.9905
D.F.ZN03425/000015 | D.F.ZN03425/000015 | 0 | Lower North Shore | CASTLE COVE |  | 400 | 3.0955 | 162.4719
D.F.ZN03425/000016 | D.F.ZN03425/000016 | 0 | Lower North Shore | CASTLE COVE |  | 295 | 2.4326 | 127.6766
D.F.ZN03425/000017 | D.F.ZN03425/000017 | 0 | Lower North Shore | CASTLE COVE |  | 370 | 4.3264 | 227.0765
D.F.ZN03425/000018 | D.F.ZN03425/000018 | 0 | Lower North Shore | CASTLE COVE |  | 370 | 3.2789 | 172.099
D.F.ZN03425/000019 | D.F.ZN03425/000019 | 0 | Lower North Shore | CASTLE COVE |  | 310 | 1.5968 | 83.8085
D.F.ZN03425/000021 | D.F.ZN03425/000021 | 0 | Lower North Shore | CASTLE COVE |  | 355 | 1.6216 | 85.1121
D.F.ZN03425/000022 | D.F.ZN03425/000022 | 0 | Lower North Shore | CASTLE COVE |  | 360 | 3.3269 | 174.6148
D.F.ZN03425/000023 | D.F.ZN03425/000023 | 0 | Lower North Shore | CASTLE COVE |  | 305 | 1.3802 | 72.4438
D.F.ZN03425/000024 | D.F.ZN03425/000024 | 0 | Lower North Shore | CASTLE COVE |  | 345 | 2.6445 | 138.798
D.F.ZN03425/000027 | D.F.ZN03425/000027 | 0 | Lower North Shore | CASTLE COVE |  | 360 | 0.5948 | 31.22
D.F.ZN03425/000028 | D.F.ZN03425/000028 | 0 | Lower North Shore | CASTLE COVE |  | 355 | 2.424 | 127.226
D.F.ZN03425/000030 | D.F.ZN03425/000030 | 0 | Lower North Shore | CASTLE COVE |  | 395 | 2.6616 | 139.6986
D.F.ZN03425/000032 | D.F.ZN03425/000032 | 0 | Lower North Shore | CASTLE COVE |  | 315 | 1.5749 | 82.659
D.F.ZN03425/000033 | D.F.ZN03425/000033 | 0 | Lower North Shore | CASTLE COVE |  | 360 | 1.4557 | 76.402
D.F.ZN03425/000034 | D.F.ZN03425/000034 | 0 | Lower North Shore | CASTLE COVE |  | 400 | 3.1548 | 165.5843
D.F.ZN03425/000035 | D.F.ZN03425/000035 | 0 | Lower North Shore | CASTLE COVE |  | 205 | 1.8876 | 99.072
D.F.ZN03425/000036 | D.F.ZN03425/000036 | 0 | Lower North Shore | CASTLE COVE |  | 355 | 2.7631 | 145.0252
D.F.ZN03425/000039 | D.F.ZN03425/000039 | 0 | Lower North Shore | CASTLE COVE |  | 190 | 1.5014 | 78.8044
D.F.ZN03425/000043 | D.F.ZN03425/000043 | 0 | Lower North Shore | CASTLE COVE |  | 345 | 3.1435 | 164.9897
D.F.ZN03425/000044 | D.F.ZN03425/000044 | 0 | Lower North Shore | CASTLE COVE |  | 345 | 2.741 | 143.8632
D.F.ZN03425/000045 | D.F.ZN03425/000045 | 0 | Lower North Shore | CASTLE COVE |  | 370 | 1.1802 | 61.9458
D.F.ZN03425/000046 | D.F.ZN03425/000046 | 0 | Lower North Shore | CASTLE COVE |  | 355 | 1.5982 | 83.8841
D.F.ZN03472/000007 | D.F.ZN03472/000007 | 0 | Canterbury Bankstown | SEFTON |  | 400 | 0.7817 | 41.0271
D.F.ZN03472/000008 | D.F.ZN03472/000008 | 0 | Canterbury Bankstown | SEFTON |  | 340 | 2.7986 | 146.8905
D.F.ZN03472/000011 | D.F.ZN03472/000011 | 0 | Canterbury Bankstown | SEFTON |  | 390 | 2.5359 | 133.0982
D.F.ZN03472/000012 | D.F.ZN03472/000012 | 0 | Canterbury Bankstown | SEFTON |  | 340 | 3.0079 | 157.8733
D.F.ZN03472/000015 | D.F.ZN03472/000015 | 0 | Canterbury Bankstown | SEFTON |  | 400 | 1.0047 | 52.7305
D.F.ZN03472/000016 | D.F.ZN03472/000016 | 0 | Canterbury Bankstown | SEFTON |  | 325 | 2.8818 | 151.2548
D.F.ZN03472/000017 | D.F.ZN03472/000017 | 0 | Canterbury Bankstown | SEFTON |  | 385 | 3.1235 | 163.9426
D.F.ZN03472/000018 | D.F.ZN03472/000018 | 0 | Canterbury Bankstown | SEFTON |  | 365 | 0.8562 | 44.9402
D.F.ZN03472/000019 | D.F.ZN03472/000019 | 0 | Canterbury Bankstown | SEFTON |  | 400 | 1.8375 | 96.4429
D.F.ZN03472/000020 | D.F.ZN03472/000020 | 0 | Canterbury Bankstown | SEFTON |  | 385 | 3.0443 | 159.7832
D.F.ZN03472/000022 | D.F.ZN03472/000022 | 0 | Canterbury Bankstown | SEFTON |  | 390 | 3.1669 | 166.2202
D.F.ZN03472/000027 | D.F.ZN03472/000027 | 0 | Canterbury Bankstown | SEFTON |  | 365 | 4.0308 | 211.5619
D.F.ZN03472/000028 | D.F.ZN03472/000028 | 0 | Canterbury Bankstown | SEFTON |  | 330 | 4.518 | 237.1311
D.F.ZN03472/000029 | D.F.ZN03472/000029 | 0 | Canterbury Bankstown | SEFTON |  | 365 | 1.9268 | 101.1312
D.F.ZN03472/000030 | D.F.ZN03472/000030 | 0 | Canterbury Bankstown | SEFTON |  | 400 | 4.6712 | 245.1746
D.F.ZN03472/000033 | D.F.ZN03472/000033 | 0 | Canterbury Bankstown | SEFTON |  | 325 | 3.42 | 179.5056
D.F.ZN03472/000034 | D.F.ZN03472/000034 | 0 | Canterbury Bankstown | SEFTON |  | 370 | 2.6225 | 137.6432
D.F.ZN03472/000035 | D.F.ZN03472/000035 | 0 | Canterbury Bankstown | SEFTON |  | 390 | 3.69 | 193.6741
D.F.ZN03672/000004 | D.F.ZN03672/000004 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 400 | 2.9893 | 156.8994
D.F.ZN03672/000006 | D.F.ZN03672/000006 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 350 | 2.6946 | 141.4309
D.F.ZN03672/000009 | D.F.ZN03672/000009 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 275 | 2.3598 | 123.8562
D.F.ZN03672/000013 | D.F.ZN03672/000013 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 350 | 2.1226 | 111.4092
D.F.ZN03672/000019 | D.F.ZN03672/000019 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 400 |  | 0
D.F.ZN03672/000021 | D.F.ZN03672/000021 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 355 | 0.0841 | 4.4115
D.F.ZN03672/000022 | D.F.ZN03672/000022 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 400 | 12.001 | 629.8894
D.F.ZN03672/000023 | D.F.ZN03672/000023 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 355 | 3.3151 | 173.9953
D.F.ZN03672/000026 | D.F.ZN03672/000026 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 310 | 0.3304 | 17.3393
D.F.ZN03672/000029 | D.F.ZN03672/000029 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 355 | 0.3711 | 19.4754
D.F.ZN03672/000032 | D.F.ZN03672/000032 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 350 | 0.1241 | 6.513
D.F.ZN03672/000034 | D.F.ZN03672/000034 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 385 | 2.6567 | 139.4431
D.F.ZN03672/000035 | D.F.ZN03672/000035 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 395 | 3.4315 | 180.1065
D.F.ZN03672/000036 | D.F.ZN03672/000036 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 385 | 3.3513 | 175.8978
D.F.ZN03672/000037 | D.F.ZN03672/000037 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 400 | 3.4467 | 180.9025
D.F.ZN03672/000042 | D.F.ZN03672/000042 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 400 | 4.007 | 210.3132
D.F.ZN03672/000043 | D.F.ZN03672/000043 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 400 | 3.5463 | 186.1306
D.F.ZN03672/000044 | D.F.ZN03672/000044 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 370 | 2.6488 | 139.025
D.F.ZN03672/000046 | D.F.ZN03672/000046 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 370 | 3.3464 | 175.6396
D.F.ZN03672/000048 | D.F.ZN03672/000048 | 0 | Eastern Suburbs Outer | MAROUBRA |  | 350 | 0.2578 | 13.5322
D.F.ZN03922/000001 | D.F.ZN03922/000001 | 0 | Inner West Sydney | DRUMMOYNE |  | 230 | 0.6381 | 33.4912
D.F.ZN03922/000002 | D.F.ZN03922/000002 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 3.5196 | 184.7307
D.F.ZN03922/000003 | D.F.ZN03922/000003 | 0 | Inner West Sydney | DRUMMOYNE |  | 225 | 1.4191 | 74.4825
D.F.ZN03922/000005 | D.F.ZN03922/000005 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 4.0471 | 212.4197
D.F.ZN03922/000007 | D.F.ZN03922/000007 | 0 | Inner West Sydney | DRUMMOYNE |  | 385 | 3.46 | 181.6014
D.F.ZN03922/000010 | D.F.ZN03922/000010 | 0 | Inner West Sydney | DRUMMOYNE |  | 385 | 2.535 | 133.0538
D.F.ZN03922/000011 | D.F.ZN03922/000011 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 3.6808 | 193.1902
D.F.ZN03922/000012 | D.F.ZN03922/000012 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 3.3879 | 177.8193
D.F.ZN03922/000013 | D.F.ZN03922/000013 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 4.6854 | 245.9194
D.F.ZN03922/000014 | D.F.ZN03922/000014 | 0 | Inner West Sydney | DRUMMOYNE |  | 320 | 3.1628 | 166.003
D.F.ZN03922/000017 | D.F.ZN03922/000017 | 0 | Inner West Sydney | DRUMMOYNE |  | 300 | 3.5924 | 188.5541
D.F.ZN03922/000018 | D.F.ZN03922/000018 | 0 | Inner West Sydney | DRUMMOYNE |  | 360 | 4.5702 | 239.8748
D.F.ZN03922/000019 | D.F.ZN03922/000019 | 0 | Inner West Sydney | DRUMMOYNE |  | 330 | 1.8306 | 96.0838
D.F.ZN03922/000021 | D.F.ZN03922/000021 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 1.8415 | 96.6516
D.F.ZN03922/000022 | D.F.ZN03922/000022 | 0 | Inner West Sydney | DRUMMOYNE |  | 355 | 1.8829 | 98.8243
D.F.ZN03922/000023 | D.F.ZN03922/000023 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 1.2767 | 67.0078
D.F.ZN03922/000026 | D.F.ZN03922/000026 | 0 | Inner West Sydney | DRUMMOYNE |  | 340 | 2.9885 | 156.8576
D.F.ZN03922/000027 | D.F.ZN03922/000027 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 1.1379 | 59.7227
D.F.ZN03922/000029 | D.F.ZN03922/000029 | 0 | Inner West Sydney | DRUMMOYNE |  | 400 | 3.895 | 204.437
D.F.ZN03922/000030 | D.F.ZN03922/000030 | 0 | Inner West Sydney | DRUMMOYNE |  | 230 | 0.2863 | 15.0248
D.F.ZN04545/000002 | D.F.ZN04545/000002 | 0 | Carlingford | MEADOWBANK |  | 325 | 3.384 | 177.6137
D.F.ZN04545/000003 | D.F.ZN04545/000003 | 0 | Carlingford | MEADOWBANK |  | 390 | 4.2054 | 220.7252
D.F.ZN04545/000004 | D.F.ZN04545/000004 | 0 | Carlingford | MEADOWBANK |  | 360 | 3.175 | 166.6461
D.F.ZN04545/000006 | D.F.ZN04545/000006 | 0 | Carlingford | MEADOWBANK |  | 390 | 2.2508 | 118.1367
D.F.ZN04545/000009 | D.F.ZN04545/000009 | 0 | Carlingford | MEADOWBANK |  | 390 | 4.6132 | 242.1304
D.F.ZN04545/000010 | D.F.ZN04545/000010 | 0 | Carlingford | MEADOWBANK |  | 330 |  | 0
D.F.ZN04545/000011 | D.F.ZN04545/000011 | 0 | Carlingford | MEADOWBANK |  | 200 | 0.7273 | 38.1713
D.F.ZN04545/000012 | D.F.ZN04545/000012 | 0 | Carlingford | MEADOWBANK |  | 335 |  | 0
D.F.ZN04545/000013 | D.F.ZN04545/000013 | 0 | Carlingford | MEADOWBANK |  | 220 | 0.4743 | 24.8937
D.F.ZN04545/000014 | D.F.ZN04545/000014 | 0 | Carlingford | MEADOWBANK |  | 335 | 9.9252 | 520.9364
D.F.ZN04545/000016 | D.F.ZN04545/000016 | 0 | Carlingford | MEADOWBANK |  | 320 | 8.3578 | 438.6723
D.F.ZN04545/000017 | D.F.ZN04545/000017 | 0 | Carlingford | MEADOWBANK |  | 400 | 1.4135 | 74.1872
D.F.ZN04545/000018 | D.F.ZN04545/000018 | 0 | Carlingford | MEADOWBANK |  | 320 |  | 0
D.F.ZN04545/000019 | D.F.ZN04545/000019 | 0 | Carlingford | MEADOWBANK |  | 345 | 3.1406 | 164.8365
D.F.ZN04545/000020 | D.F.ZN04545/000020 | 0 | Carlingford | MEADOWBANK |  | 340 |  | 0
D.F.ZN04545/000021 | D.F.ZN04545/000021 | 0 | Carlingford | MEADOWBANK |  | 230 | 1.7248 | 90.5292
D.F.ZN04545/000024 | D.F.ZN04545/000024 | 0 | Carlingford | MEADOWBANK |  | 400 | 1.1061 | 58.0529
D.F.ZN04545/000025 | D.F.ZN04545/000025 | 0 | Carlingford | MEADOWBANK |  | 385 | 2.4099 | 126.4887
D.F.ZN04545/000026 | D.F.ZN04545/000026 | 0 | Carlingford | MEADOWBANK |  | 315 | 3.637 | 190.8914
D.F.ZN04545/000027 | D.F.ZN04545/000027 | 0 | Carlingford | MEADOWBANK |  | 400 | 1.7917 | 94.042
D.F.ZN04545/000028 | D.F.ZN04545/000028 | 0 | Carlingford | MEADOWBANK |  | 340 | 1.2806 | 67.2136
D.F.ZN04545/000029 | D.F.ZN04545/000029 | 0 | Carlingford | MEADOWBANK |  | 400 | 3.6247 | 190.2483
D.F.ZN04545/000031 | D.F.ZN04545/000031 | 0 | Carlingford | MEADOWBANK |  | 390 | 5.5755 | 292.6382
D.F.ZN04545/000032 | D.F.ZN04545/000032 | 0 | Carlingford | MEADOWBANK |  | 400 | 3.1903 | 167.4499
D.F.ZN04545/000033 | D.F.ZN04545/000033 | 0 | Carlingford | MEADOWBANK |  | 390 | 1.8192 | 95.4814
D.F.ZN04545/000035 | D.F.ZN04545/000035 | 0 | Carlingford | MEADOWBANK |  | 330 | 2.9051 | 152.477
D.F.ZN04545/000036 | D.F.ZN04545/000036 | 0 | Carlingford | MEADOWBANK |  | 330 | 3.2496 | 170.5581
D.F.ZN04545/000039 | D.F.ZN04545/000039 | 0 | Carlingford | MEADOWBANK |  | 390 | 0.8191 | 42.9927
D.F.ZN04545/000040 | D.F.ZN04545/000040 | 0 | Carlingford | MEADOWBANK |  | 390 | 3.7079 | 194.6122
D.F.ZN04545/000041 | D.F.ZN04545/000041 | 0 | Carlingford | MEADOWBANK |  | 390 | 2.6203 | 137.5279
D.F.ZN04545/000042 | D.F.ZN04545/000042 | 0 | Carlingford | MEADOWBANK |  | 400 | 2.5255 | 132.5538
D.F.ZN04545/000044 | D.F.ZN04545/000044 | 0 | Carlingford | MEADOWBANK |  | 390 | 4.4025 | 231.069
D.F.ZN04853/000002 | D.F.ZN04853/000002 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 400 | 2.4716 | 129.7255
D.F.ZN04853/000004 | D.F.ZN04853/000004 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 215 | 2.8527 | 149.7276
D.F.ZN04853/000007 | D.F.ZN04853/000007 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 400 | 1.068 | 56.057
D.F.ZN04853/000008 | D.F.ZN04853/000008 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 215 | 0.7727 | 40.5544
D.F.ZN04853/000011 | D.F.ZN04853/000011 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 215 | 1.4301 | 75.0587
D.F.ZN04853/000012 | D.F.ZN04853/000012 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 195 | 2.1311 | 111.8536
D.F.ZN04853/000015 | D.F.ZN04853/000015 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 400 | 3.4387 | 180.4856
D.F.ZN04853/000016 | D.F.ZN04853/000016 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 400 | 2.4312 | 127.6041
D.F.ZN04853/000017 | D.F.ZN04853/000017 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 210 | 1.6695 | 87.6236
D.F.ZN04853/000022 | D.F.ZN04853/000022 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 315 | 3.0838 | 161.859
D.F.ZN04853/000023 | D.F.ZN04853/000023 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 315 | 2.0502 | 107.6059
D.F.ZN04853/000026 | D.F.ZN04853/000026 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 400 | 3.9684 | 208.2848
D.F.ZN04853/000027 | D.F.ZN04853/000027 | 0 | Canterbury Bankstown | STRATHFIELD SOUTH |  | 315 | 1.5282 | 80.2086
D.F.ZN04990/00051L | D.F.ZN04990/000051 | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.331 | 174.8337
D.F.ZN04990/00052L | D.F.ZN04990/000052 | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.0255 | 158.7961
D.F.ZN04990/00054L | D.F.ZN04990/000054 | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.3024 | 173.3314
D.F.ZN04990/00055L | D.F.ZN04990/000055 | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.6086 | 31.9454
D.F.ZN04990/00056L | D.F.ZN04990/000056 | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.6806 | 140.6945
D.F.ZN04990/00057L | D.F.ZN04990/000057 | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.1393 | 7.3089
D.F.ZN04990/00051A | D.F.ZN04990/00051A | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.461 | 129.171
D.F.ZN04990/00051B | D.F.ZN04990/00051B | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.8023 | 147.0847
D.F.ZN04990/00051C | D.F.ZN04990/00051C | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.051 | 55.1658
D.F.ZN04990/00051D | D.F.ZN04990/00051D | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.0189 | 105.9647
D.F.ZN04990/00051F | D.F.ZN04990/00051F | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.2491 | 170.5335
D.F.ZN04990/00051G | D.F.ZN04990/00051G | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.749 | 39.312
D.F.ZN04990/00051H | D.F.ZN04990/00051H | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 4.3612 | 228.9022
D.F.ZN04990/00051J | D.F.ZN04990/00051J | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.7218 | 142.8548
D.F.ZN04990/00051K | D.F.ZN04990/00051K | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.0752 | 161.4073
D.F.ZN04990/00051M | D.F.ZN04990/00051M | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.7152 | 194.9989
D.F.ZN04990/00052A | D.F.ZN04990/00052A | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.95 | 49.8613
D.F.ZN04990/00052B | D.F.ZN04990/00052B | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.3669 | 124.2312
D.F.ZN04990/00052C | D.F.ZN04990/00052C | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.0905 | 109.7245
D.F.ZN04990/00052D | D.F.ZN04990/00052D | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.3781 | 72.3309
D.F.ZN04990/00052E | D.F.ZN04990/00052E | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.5219 | 27.3927
D.F.ZN04990/00052F | D.F.ZN04990/00052F | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.9979 | 104.8626
D.F.ZN04990/00052G | D.F.ZN04990/00052G | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 4.3639 | 229.0455
D.F.ZN04990/00052J | D.F.ZN04990/00052J | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.6477 | 86.4793
D.F.ZN04990/00052K | D.F.ZN04990/00052K | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.8511 | 44.671
D.F.ZN04990/00052M | D.F.ZN04990/00052M | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.2561 | 13.4413
D.F.ZN04990/00053A | D.F.ZN04990/00053A | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.5979 | 188.841
D.F.ZN04990/00053B | D.F.ZN04990/00053B | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.2579 | 118.5065
D.F.ZN04990/00053C | D.F.ZN04990/00053C | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.1055 | 58.0218
D.F.ZN04990/00053D | D.F.ZN04990/00053D | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.9354 | 101.5828
D.F.ZN04990/00053F | D.F.ZN04990/00053F | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.9662 | 50.7143
D.F.ZN04990/00053G | D.F.ZN04990/00053G | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.0046 | 105.2116
D.F.ZN04990/00053H | D.F.ZN04990/00053H | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.1091 | 58.2127
D.F.ZN04990/00053J | D.F.ZN04990/00053J | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.7459 | 39.1471
D.F.ZN04990/00054B | D.F.ZN04990/00054B | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.6565 | 34.4592
D.F.ZN04990/00054C | D.F.ZN04990/00054C | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.2159 | 116.3026
D.F.ZN04990/00054D | D.F.ZN04990/00054D | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.2903 | 120.2082
D.F.ZN04990/00054E | D.F.ZN04990/00054E | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.3088 | 121.1821
D.F.ZN04990/00054F | D.F.ZN04990/00054F | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.8998 | 204.6852
D.F.ZN04990/00054G | D.F.ZN04990/00054G | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.6512 | 34.1805
D.F.ZN04990/00054H | D.F.ZN04990/00054H | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.3429 | 175.459
D.F.ZN04990/00054J | D.F.ZN04990/00054J | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.8913 | 204.2387
D.F.ZN04990/00054K | D.F.ZN04990/00054K | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.5516 | 28.9529
D.F.ZN04990/00054M | D.F.ZN04990/00054M | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.8971 | 47.0871
D.F.ZN04990/00055C | D.F.ZN04990/00055C | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.9873 | 209.2799
D.F.ZN04990/00055D | D.F.ZN04990/00055D | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.1579 | 113.2629
D.F.ZN04990/00055E | D.F.ZN04990/00055E | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.7651 | 92.6441
D.F.ZN04990/00055F | D.F.ZN04990/00055F | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.6427 | 33.7306
D.F.ZN04990/00055G | D.F.ZN04990/00055G | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.6957 | 88.9999
D.F.ZN04990/00055H | D.F.ZN04990/00055H | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.6812 | 35.7532
D.F.ZN04990/00055J | D.F.ZN04990/00055J | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 5.9736 | 313.5308
D.F.ZN04990/00055K | D.F.ZN04990/00055K | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.8576 | 149.9868
D.F.ZN04990/00055M | D.F.ZN04990/00055M | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 3.2828 | 172.3028
D.F.ZN04990/00056A | D.F.ZN04990/00056A | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.4608 | 24.1845
D.F.ZN04990/00056C | D.F.ZN04990/00056C | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.604 | 84.1881
D.F.ZN04990/00056D | D.F.ZN04990/00056D | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 2.7581 | 144.7606
D.F.ZN04990/00056E | D.F.ZN04990/00056E | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.5756 | 82.6955
D.F.ZN04990/00056G | D.F.ZN04990/00056G | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.2915 | 15.2989
D.F.ZN04990/00056H | D.F.ZN04990/00056H | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.0401 | 2.1027
D.F.ZN04990/00056J | D.F.ZN04990/00056J | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.029 | 54.0102
D.F.ZN04990/00056K | D.F.ZN04990/00056K | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.8215 | 95.6062
D.F.ZN04990/00057B | D.F.ZN04990/00057B | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.8814 | 46.2615
D.F.ZN04990/00057E | D.F.ZN04990/00057E | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.5686 | 82.3301
D.F.ZN04990/00057K | D.F.ZN04990/00057K | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 0.7117 | 37.3562
D.F.ZN04990/00057M | D.F.ZN04990/00057M | 0 | Sydney CBD | CITY CENTRAL | 1 | 300 | 1.6127 | 84.646
D.F.ZN05868/00002L | D.F.ZN05868/000002 | 0 | Lower North Shore | GORE HILL |  | 205 | 1.4115 | 74.0827
D.F.ZN05868/00002R | D.F.ZN05868/000002 | 1 | Lower North Shore | GORE HILL |  | 390 | 0.916 | 48.0778
D.F.ZN05868/000003 | D.F.ZN05868/000003 | 0 | Lower North Shore | GORE HILL |  | 400 | 5.5373 | 290.635
D.F.ZN05868/00005L | D.F.ZN05868/000005 | 0 | Lower North Shore | GORE HILL |  | 230 | 1.5468 | 81.1867
D.F.ZN05868/000006 | D.F.ZN05868/000006 | 0 | Lower North Shore | GORE HILL |  | 340 | 2.6024 | 136.5891
D.F.ZN05868/000007 | D.F.ZN05868/000007 | 0 | Lower North Shore | GORE HILL |  | 315 | 3.4132 | 179.1484
D.F.ZN05868/000008 | D.F.ZN05868/000008 | 0 | Lower North Shore | GORE HILL |  | 400 | 0.3274 | 17.1845
D.F.ZN05868/000009 | D.F.ZN05868/000009 | 0 | Lower North Shore | GORE HILL | 1 | 300 | 4.2023 | 220.5642
D.F.ZN05868/000010 | D.F.ZN05868/000010 | 0 | Lower North Shore | GORE HILL |  | 400 | 2.5457 | 133.6139
D.F.ZN05868/00012L | D.F.ZN05868/000012 | 0 | Lower North Shore | GORE HILL |  | 350 |  | 0
D.F.ZN05868/000013 | D.F.ZN05868/000013 | 0 | Lower North Shore | GORE HILL |  | 330 | 2.0197 | 106.0047
D.F.ZN05868/000014 | D.F.ZN05868/000014 | 0 | Lower North Shore | GORE HILL |  | 380 | 2.9931 | 157.0981
D.F.ZN05868/000015 | D.F.ZN05868/000015 | 0 | Lower North Shore | GORE HILL |  | 400 | 0.528 | 27.7128
D.F.ZN05868/000017 | D.F.ZN05868/000017 | 0 | Lower North Shore | GORE HILL |  | 400 | 1.5357 | 80.6032
D.F.ZN05868/000018 | D.F.ZN05868/000018 | 0 | Lower North Shore | GORE HILL |  | 335 | 0.9128 | 47.9085
D.F.ZN05868/000020 | D.F.ZN05868/000020 | 0 | Lower North Shore | GORE HILL |  |  |  | 0
D.F.ZN05868/000021 | D.F.ZN05868/000021 | 0 | Lower North Shore | GORE HILL |  | 385 | 2.8357 | 148.8347
D.F.ZN05868/000022 | D.F.ZN05868/000022 | 0 | Lower North Shore | GORE HILL |  | 400 | 2.6133 | 137.1645
D.F.ZN05868/000023 | D.F.ZN05868/000023 | 0 | Lower North Shore | GORE HILL |  | 340 | 1.6534 | 86.7805
D.F.ZN05868/000024 | D.F.ZN05868/000024 | 0 | Lower North Shore | GORE HILL |  | 400 | 4.0299 | 211.5157
D.F.ZN05868/000025 | D.F.ZN05868/000025 | 0 | Lower North Shore | GORE HILL |  | 320 | 1.8077 | 94.8785
D.F.ZN05868/000027 | D.F.ZN05868/000027 | 0 | Lower North Shore | GORE HILL |  | 390 | 2.2228 | 116.6651
D.F.ZN05868/000028 | D.F.ZN05868/000028 | 0 | Lower North Shore | GORE HILL |  | 400 | 2.5913 | 136.0093
D.F.ZN05868/000030 | D.F.ZN05868/000030 | 0 | Lower North Shore | GORE HILL |  | 390 | 3.9233 | 205.9211
D.F.ZN05868/000031 | D.F.ZN05868/000031 | 0 | Lower North Shore | GORE HILL |  | 330 | 5.9246 | 310.9609
D.F.ZN05959/00003L | D.F.ZN05959/000003 | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 1.039 | 54.5351
D.F.ZN05959/00005L | D.F.ZN05959/000005 | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 4.2776 | 224.5138
D.F.ZN05959/00003D | D.F.ZN05959/00003D | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 0.8862 | 46.512
D.F.ZN05959/00003E | D.F.ZN05959/00003E | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 3.5228 | 184.8975
D.F.ZN05959/00003F | D.F.ZN05959/00003F | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 1.8279 | 95.939
D.F.ZN05959/00003K | D.F.ZN05959/00003K | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 4.0107 | 210.5088
D.F.ZN05959/00005D | D.F.ZN05959/00005D | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 6.6904 | 351.1552
D.F.ZN05959/00005E | D.F.ZN05959/00005E | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 1.2621 | 66.2457
D.F.ZN05959/00005F | D.F.ZN05959/00005F | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 3.3592 | 176.3104
D.F.ZN05959/00005K | D.F.ZN05959/00005K | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 6.3032 | 330.8345
D.F.ZN05959/00005M | D.F.ZN05959/00005M | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 1.9094 | 100.2151
D.F.ZN05959/00007A | D.F.ZN05959/00007A | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 3.0478 | 159.9697
D.F.ZN05959/00007B | D.F.ZN05959/00007B | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 1.7587 | 92.3092
D.F.ZN05959/00007C | D.F.ZN05959/00007C | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 2.9084 | 152.6523
D.F.ZN05959/00007G | D.F.ZN05959/00007G | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 5.2971 | 278.0239
D.F.ZN05959/00007H | D.F.ZN05959/00007H | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 2.7612 | 144.9254
D.F.ZN05959/00007J | D.F.ZN05959/00007J | 0 | Sydney CBD | BELMORE PARK | 1 | 300 | 0.6843 | 35.9164
D.F.ZN07481/00001R | D.F.ZN07481/000001 | 0 | Camperdown | DARLING HARBOUR |  | 270 | 2.7797 | 145.8965
D.F.ZN07481/000002 | D.F.ZN07481/000002 | 0 | Camperdown | DARLING HARBOUR |  | 400 | 2.0546 | 107.8372
D.F.ZN07481/00003L | D.F.ZN07481/000003 | 0 | Camperdown | DARLING HARBOUR |  | 340 | 3.7663 | 197.6818
D.F.ZN07481/00003R | D.F.ZN07481/000003 | 1 | Camperdown | DARLING HARBOUR |  | 400 | 1.4849 | 77.9364
D.F.ZN07481/000005 | D.F.ZN07481/000005 | 0 | Camperdown | DARLING HARBOUR |  | 340 | 0.5135 | 26.9528
D.F.ZN07481/00006R | D.F.ZN07481/000006 | 0 | Camperdown | DARLING HARBOUR |  | 370 | 5.0365 | 264.3476
D.F.ZN07481/00006L | D.F.ZN07481/000006 | 1 | Camperdown | DARLING HARBOUR |  | 340 | 2.318 | 121.6624
D.F.ZN07481/000008 | D.F.ZN07481/000008 | 0 | Camperdown | DARLING HARBOUR |  | 340 | 3.3085 | 173.6527
D.F.ZN07481/00009L | D.F.ZN07481/000009 | 0 | Camperdown | DARLING HARBOUR |  | 370 | 3.3083 | 173.6394 | 1 | 286.8002
D.F.ZN07481/00009R | D.F.ZN07481/000009 | 1 | Camperdown | DARLING HARBOUR |  | 400 | 2.156 | 113.1608 | 1
D.F.ZN07481/000010 | D.F.ZN07481/000010 | 0 | Camperdown | DARLING HARBOUR |  | 365 | 1.5364 | 80.6411
D.F.ZN07481/00012R | D.F.ZN07481/000012 | 0 | Camperdown | DARLING HARBOUR |  | 325 | 3.0103 | 157.999
D.F.ZN07481/00012L | D.F.ZN07481/000012 | 1 | Camperdown | DARLING HARBOUR |  | 290 | 3.0166 | 158.3301
D.F.ZN07481/000013 | D.F.ZN07481/000013 | 0 | Camperdown | DARLING HARBOUR |  | 400 | 6.3581 | 333.7154
D.F.ZN07481/00014R | D.F.ZN07481/000014 | 0 | Camperdown | DARLING HARBOUR |  | 325 | 3.5114 | 184.3015
D.F.ZN07481/00014L | D.F.ZN07481/000014 | 1 | Camperdown | DARLING HARBOUR |  | 340 | 3.11 | 163.234
D.F.ZN07481/000016 | D.F.ZN07481/000016 | 0 | Camperdown | DARLING HARBOUR |  | 385 | 0.6902 | 36.2256
D.F.ZN07481/00017L | D.F.ZN07481/000017 | 0 | Camperdown | DARLING HARBOUR |  | 325 | 3.0419 | 159.6582
D.F.ZN07481/00017R | D.F.ZN07481/000017 | 1 | Camperdown | DARLING HARBOUR |  | 260 | 2.3601 | 123.8749
D.F.ZN07481/000019 | D.F.ZN07481/000019 | 0 | Camperdown | DARLING HARBOUR |  | 385 | 2.4542 | 128.8126
D.F.ZN07481/00020R | D.F.ZN07481/000020 | 0 | Camperdown | DARLING HARBOUR |  | 270 | 3.1516 | 165.4158
D.F.ZN07481/00020L | D.F.ZN07481/000020 | 1 | Camperdown | DARLING HARBOUR |  | 360 | 1.5013 | 78.7961
D.F.ZN07481/000021 | D.F.ZN07481/000021 | 0 | Camperdown | DARLING HARBOUR |  | 325 | 2.9965 | 157.2734
D.F.ZN07900/000001 | D.F.ZN07900/000001 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 310 | 1.4088 | 73.942
D.F.ZN07900/00002R | D.F.ZN07900/000002 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 290 | 2.8411 | 149.1169
D.F.ZN07900/00002L | D.F.ZN07900/000002 | 1 | Eastern Suburbs Inner | CAMPBELL ST |  | 270 | 2.2758 | 119.451
D.F.ZN07900/000003 | D.F.ZN07900/000003 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 400 | 1.4091 | 73.9588
D.F.ZN07900/00004R | D.F.ZN07900/000004 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 305 | 2.5462 | 133.6416
D.F.ZN07900/00004L | D.F.ZN07900/000004 | 1 | Eastern Suburbs Inner | CAMPBELL ST |  | 305 | 0.752 | 39.4717
D.F.ZN07900/000006 | D.F.ZN07900/000006 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 350 | 2.1571 | 113.2181
D.F.ZN07900/00007L | D.F.ZN07900/000007 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 315 | 3.5135 | 184.413
D.F.ZN07900/00007R | D.F.ZN07900/000007 | 1 | Eastern Suburbs Inner | CAMPBELL ST |  | 305 | 0.7748 | 40.6674
D.F.ZN07900/000009 | D.F.ZN07900/000009 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 400 | 1.085 | 56.9488
D.F.ZN07900/00010R | D.F.ZN07900/000010 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 360 | 2.3733 | 124.5665
D.F.ZN07900/00010L | D.F.ZN07900/000010 | 1 | Eastern Suburbs Inner | CAMPBELL ST |  | 295 | 2.0238 | 106.2228
D.F.ZN07900/000011 | D.F.ZN07900/000011 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 400 | 2.9592 | 155.3171
D.F.ZN07900/000012 | D.F.ZN07900/000012 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 340 | 4.5445 | 238.5262
D.F.ZN07900/000014 | D.F.ZN07900/000014 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 325 | 1.6169 | 84.8662
D.F.ZN07900/000015 | D.F.ZN07900/000015 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 385 | 1.3673 | 71.7669
D.F.ZN07900/000016 | D.F.ZN07900/000016 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 295 | 1.1982 | 62.8901
D.F.ZN07900/00017L | D.F.ZN07900/000017 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 315 | 2.4173 | 126.8731
D.F.ZN07900/000019 | D.F.ZN07900/000019 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 400 | 0.637 | 33.4341
D.F.ZN07900/00020R | D.F.ZN07900/000020 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 290 | 1.9337 | 101.4933
D.F.ZN07900/00020L | D.F.ZN07900/000020 | 1 | Eastern Suburbs Inner | CAMPBELL ST |  | 367 | 2.0243 | 106.248
D.F.ZN07900/000022 | D.F.ZN07900/000022 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 274 | 0.9725 | 51.0439
D.F.ZN07900/00023R | D.F.ZN07900/000023 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 300 | 2.6064 | 136.798
D.F.ZN07900/00023L | D.F.ZN07900/000023 | 1 | Eastern Suburbs Inner | CAMPBELL ST |  | 400 | 1.9899 | 104.4401
D.F.ZN07900/000024 | D.F.ZN07900/000024 | 0 | Eastern Suburbs Inner | CAMPBELL ST |  | 400 | 2.9936 | 157.1215
D.F.ZN08000/00002L | D.F.ZN08000/000002 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 4.08 | 214.1445
D.F.ZN08000/00002R | D.F.ZN08000/000002 | 1 | Carlingford | MACQUARIE PARK |  | 320 | 1.9608 | 102.916
D.F.ZN08000/000003 | D.F.ZN08000/000003 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 3.2351 | 169.7987
D.F.ZN08000/000004 | D.F.ZN08000/000004 | 0 | Carlingford | MACQUARIE PARK |  | 325 | 0.9889 | 51.9017
D.F.ZN08000/000006 | D.F.ZN08000/000006 | 0 | Carlingford | MACQUARIE PARK |  | 320 | 2.5485 | 133.7595
D.F.ZN08000/00007L | D.F.ZN08000/000007 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 3.7824 | 198.5237
D.F.ZN08000/00007R | D.F.ZN08000/000007 | 1 | Carlingford | MACQUARIE PARK |  | 365 | 1.9829 | 104.0762
D.F.ZN08000/000008 | D.F.ZN08000/000008 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 3.4296 | 180.0073
D.F.ZN08000/00010L | D.F.ZN08000/000010 | 0 | Carlingford | MACQUARIE PARK |  | 365 | 1.7121 | 89.8628
D.F.ZN08000/00010R | D.F.ZN08000/000010 | 1 | Carlingford | MACQUARIE PARK |  | 385 | 2.1976 | 115.344
D.F.ZN08000/000011 | D.F.ZN08000/000011 | 0 | Carlingford | MACQUARIE PARK |  | 325 | 2.8278 | 148.421
D.F.ZN08000/000012 | D.F.ZN08000/000012 | 0 | Carlingford | MACQUARIE PARK |  | 380 | 2.3784 | 124.832
D.F.ZN08000/000014 | D.F.ZN08000/000014 | 0 | Carlingford | MACQUARIE PARK |  | 375 | 2.6174 | 137.3798
D.F.ZN08000/000015 | D.F.ZN08000/000015 | 0 | Carlingford | MACQUARIE PARK |  | 310 | 2.4336 | 127.7314
D.F.ZN08000/000016 | D.F.ZN08000/000016 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 3.5118 | 184.3217
D.F.ZN08000/00017R | D.F.ZN08000/000017 | 0 | Carlingford | MACQUARIE PARK |  | 355 | 3.2058 | 168.2631
D.F.ZN08000/00017L | D.F.ZN08000/000017 | 1 | Carlingford | MACQUARIE PARK |  | 365 | 0.6212 | 32.6029
D.F.ZN08000/000019 | D.F.ZN08000/000019 | 0 | Carlingford | MACQUARIE PARK |  | 355 | 2.4136 | 126.6789
D.F.ZN08000/00020L | D.F.ZN08000/000020 | 0 | Carlingford | MACQUARIE PARK |  | 350 | 2.3258 | 122.0748
D.F.ZN08000/00020R | D.F.ZN08000/000020 | 1 | Carlingford | MACQUARIE PARK |  | 315 |  | 0
D.F.ZN08000/000021 | D.F.ZN08000/000021 | 0 | Carlingford | MACQUARIE PARK |  | 400 |  | 0
D.F.ZN08000/00023R | D.F.ZN08000/000023 | 0 | Carlingford | MACQUARIE PARK |  | 375 | 1.3518 | 70.951
D.F.ZN08000/00023L | D.F.ZN08000/000023 | 1 | Carlingford | MACQUARIE PARK |  | 350 | 0.0477 | 2.5043
D.F.ZN08000/00024R | D.F.ZN08000/000024 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 2.9221 | 153.3679
D.F.ZN08000/00025R | D.F.ZN08000/000025 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 2.6425 | 138.6953
D.F.ZN08000/00025L | D.F.ZN08000/000025 | 1 | Carlingford | MACQUARIE PARK |  | 305 | 0.9865 | 51.7753
D.F.ZN08000/000028 | D.F.ZN08000/000028 | 0 | Carlingford | MACQUARIE PARK |  | 370 | 2.0609 | 108.1694
D.F.ZN08000/00029L | D.F.ZN08000/000029 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 0.4798 | 25.1817
D.F.ZN08000/00029R | D.F.ZN08000/000029 | 1 | Carlingford | MACQUARIE PARK |  | 350 | 0.3713 | 19.4868
D.F.ZN08000/000030 | D.F.ZN08000/000030 | 0 | Carlingford | MACQUARIE PARK |  | 355 | 1.8703 | 98.1632
D.F.ZN08000/00034R | D.F.ZN08000/000034 | 0 | Carlingford | MACQUARIE PARK |  | 375 | 1.8651 | 97.8926
D.F.ZN08000/00034L | D.F.ZN08000/000034 | 1 | Carlingford | MACQUARIE PARK |  | 400 | 0.3102 | 16.2796
D.F.ZN08000/000036 | D.F.ZN08000/000036 | 0 | Carlingford | MACQUARIE PARK |  | 400 | 4.2745 | 224.3518
D.F.ZN08000/000038 | D.F.ZN08000/000038 | 0 | Carlingford | MACQUARIE PARK |  | 310 | 3.5281 | 185.1769
D.F.ZN08000/000039 | D.F.ZN08000/000039 | 0 | Carlingford | MACQUARIE PARK |  | 280 | 18.9235 | 993.2277
D.F.ZN08100/000001 | D.F.ZN08100/000001 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 290 | 0.966 | 50.7008
D.F.ZN08100/000002 | D.F.ZN08100/000002 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 360 | 2.3237 | 121.9639
D.F.ZN08100/00004R | D.F.ZN08100/000004 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 3.2295 | 169.5051
D.F.ZN08100/00004L | D.F.ZN08100/000004 | 1 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 1.856 | 97.4147
D.F.ZN08100/000006 | D.F.ZN08100/000006 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 2.619 | 137.4615
D.F.ZN08100/000007 | D.F.ZN08100/000007 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 2.1383 | 112.2327
D.F.ZN08100/000009 | D.F.ZN08100/000009 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 340 | 1.9466 | 102.1675
D.F.ZN08100/000010 | D.F.ZN08100/000010 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 290 | 1.6534 | 86.7791
D.F.ZN08100/000011 | D.F.ZN08100/000011 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 360 | 2.4359 | 127.8518
D.F.ZN08100/00012R | D.F.ZN08100/000012 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 1.408 | 73.9012
D.F.ZN08100/00012L | D.F.ZN08100/000012 | 1 | Eastern Suburbs Inner | GREEN SQUARE |  | 295 | 0.6499 | 34.1134
D.F.ZN08100/000014 | D.F.ZN08100/000014 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 275 | 2.4199 | 127.0129
D.F.ZN08100/00017R | D.F.ZN08100/000017 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 350 | 2.8587 | 150.0434
D.F.ZN08100/00017L | D.F.ZN08100/000017 | 1 | Eastern Suburbs Inner | GREEN SQUARE |  | 330 | 1.5188 | 79.7157
D.F.ZN08100/000019 | D.F.ZN08100/000019 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 1.2509 | 65.6554
D.F.ZN08100/00020L | D.F.ZN08100/000020 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 330 | 2.0463 | 107.4042
D.F.ZN08100/000022 | D.F.ZN08100/000022 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 290 | 2.7898 | 146.4246
D.F.ZN08100/000024 | D.F.ZN08100/000024 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 345 | 1.5899 | 83.4496
D.F.ZN08100/00025L | D.F.ZN08100/000025 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 245 | 1.5337 | 80.4962
D.F.ZN08100/000028 | D.F.ZN08100/000028 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 2.5067 | 131.5667
D.F.ZN08100/00029L | D.F.ZN08100/000029 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 3.1666 | 166.2034
D.F.ZN08100/000030 | D.F.ZN08100/000030 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 280 | 3.0722 | 161.2467
D.F.ZN08100/00031L | D.F.ZN08100/000031 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 400 | 2.5302 | 132.8032
D.F.ZN08100/000033 | D.F.ZN08100/000033 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 260 | 1.6375 | 85.945
D.F.ZN08100/00034L | D.F.ZN08100/000034 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 325 | 1.8247 | 95.77
D.F.ZN08100/000036 | D.F.ZN08100/000036 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 355 | 4.6038 | 241.6368
D.F.ZN08100/00037L | D.F.ZN08100/000037 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 345 | 1.5745 | 82.6422
D.F.ZN08100/000038 | D.F.ZN08100/000038 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 265 | 3.9717 | 208.4577
D.F.ZN08100/00039L | D.F.ZN08100/000039 | 0 | Eastern Suburbs Inner | GREEN SQUARE |  | 275 | 1.3459 | 70.6405
D.F.ZN08700/00061L | D.F.ZN08700/000061 | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 4.1196 | 216.2246
D.F.ZN08700/00062L | D.F.ZN08700/000062 | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.2219 | 11.6489
D.F.ZN08700/00063L | D.F.ZN08700/000063 | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.6116 | 84.5892
D.F.ZN08700/00065L | D.F.ZN08700/000065 | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.0467 | 107.4251
D.F.ZN08700/00061A | D.F.ZN08700/00061A | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.0397 | 54.5678
D.F.ZN08700/00061B | D.F.ZN08700/00061B | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.9854 | 51.7209
D.F.ZN08700/00061C | D.F.ZN08700/00061C | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.3615 | 71.4586
D.F.ZN08700/00061D | D.F.ZN08700/00061D | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.2862 | 15.0207
D.F.ZN08700/00061E | D.F.ZN08700/00061E | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.1012 | 110.2857
D.F.ZN08700/00061F | D.F.ZN08700/00061F | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.7283 | 38.2253
D.F.ZN08700/00061G | D.F.ZN08700/00061G | 0 | Sydney CBD | CITY NORTH |  |  |  | 0
D.F.ZN08700/00061H | D.F.ZN08700/00061H | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.8479 | 96.9887
D.F.ZN08700/00061J | D.F.ZN08700/00061J | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.6866 | 88.5222
D.F.ZN08700/00061K | D.F.ZN08700/00061K | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.3665 | 19.2352
D.F.ZN08700/00061M | D.F.ZN08700/00061M | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.0356 | 159.3293
D.F.ZN08700/00062A | D.F.ZN08700/00062A | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.0258 | 106.3294
D.F.ZN08700/00062C | D.F.ZN08700/00062C | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.1983 | 115.3808
D.F.ZN08700/00062D | D.F.ZN08700/00062D | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.2054 | 10.7811
D.F.ZN08700/00062E | D.F.ZN08700/00062E | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.7766 | 93.2479
D.F.ZN08700/00062G | D.F.ZN08700/00062G | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.3299 | 69.8035
D.F.ZN08700/00062H | D.F.ZN08700/00062H | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.8726 | 45.801
D.F.ZN08700/00062J | D.F.ZN08700/00062J | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.6444 | 86.3071
D.F.ZN08700/00062K | D.F.ZN08700/00062K | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.8987 | 204.6306
D.F.ZN08700/00062M | D.F.ZN08700/00062M | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.4051 | 73.7494
D.F.ZN08700/00063A | D.F.ZN08700/00063A | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.2584 | 66.0465
D.F.ZN08700/00063B | D.F.ZN08700/00063B | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.6016 | 136.5465
D.F.ZN08700/00063C | D.F.ZN08700/00063C | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 6.046 | 317.3304
D.F.ZN08700/00063D | D.F.ZN08700/00063D | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 6.1001 | 320.1746
D.F.ZN08700/00063E | D.F.ZN08700/00063E | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.5083 | 26.6813
D.F.ZN08700/00063F | D.F.ZN08700/00063F | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.8465 | 96.9186
D.F.ZN08700/00063G | D.F.ZN08700/00063G | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.1174 | 111.136
D.F.ZN08700/00063H | D.F.ZN08700/00063H | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.2083 | 115.9067
D.F.ZN08700/00063K | D.F.ZN08700/00063K | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.9801 | 51.4423
D.F.ZN08700/00063M | D.F.ZN08700/00063M | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.0804 | 4.2202
D.F.ZN08700/00064A | D.F.ZN08700/00064A | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.6222 | 85.1449
D.F.ZN08700/00064B | D.F.ZN08700/00064B | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.0446 | 159.7976
D.F.ZN08700/00064C | D.F.ZN08700/00064C | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.8863 | 99.0064
D.F.ZN08700/00064D | D.F.ZN08700/00064D | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 4.0242 | 211.2146
D.F.ZN08700/00064E | D.F.ZN08700/00064E | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.1496 | 60.338
D.F.ZN08700/00064F | D.F.ZN08700/00064F | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.0413 | 107.142
D.F.ZN08700/00065A | D.F.ZN08700/00065A | 0 | Sydney CBD | CITY NORTH |  |  |  | 0
D.F.ZN08700/00065B | D.F.ZN08700/00065B | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.9492 | 154.7945
D.F.ZN08700/00065C | D.F.ZN08700/00065C | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.6541 | 139.3017
D.F.ZN08700/00065D | D.F.ZN08700/00065D | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.0161 | 105.8177
D.F.ZN08700/00065E | D.F.ZN08700/00065E | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.4819 | 130.2645
D.F.ZN08700/00065G | D.F.ZN08700/00065G | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.3313 | 69.8763
D.F.ZN08700/00065H | D.F.ZN08700/00065H | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.6087 | 31.9466
D.F.ZN08700/00065J | D.F.ZN08700/00065J | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.7493 | 91.8135
D.F.ZN08700/00065K | D.F.ZN08700/00065K | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.8573 | 97.4812
D.F.ZN08700/00065M | D.F.ZN08700/00065M | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.0829 | 161.8077
D.F.ZN08700/00066A | D.F.ZN08700/00066A | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.0229 | 106.175
D.F.ZN08700/00066B | D.F.ZN08700/00066B | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 4.5137 | 236.9094
D.F.ZN08700/00066C | D.F.ZN08700/00066C | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.8312 | 96.1137
D.F.ZN08700/00066D | D.F.ZN08700/00066D | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.4328 | 180.1736
D.F.ZN08700/00066F | D.F.ZN08700/00066F | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.131 | 6.8739
D.F.ZN08700/00066G | D.F.ZN08700/00066G | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.3472 | 175.6821
D.F.ZN08700/00066H | D.F.ZN08700/00066H | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 1.2909 | 67.7567
D.F.ZN08700/00066J | D.F.ZN08700/00066J | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 0.7978 | 41.8729
D.F.ZN08700/00067H | D.F.ZN08700/00067H | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 3.1482 | 165.2399
D.F.ZN08700/00067J | D.F.ZN08700/00067J | 0 | Sydney CBD | CITY NORTH | 1 | 300 | 2.665 | 139.8737
D.F.ZN09015/000001 | D.F.ZN09015/000001 | 0 | #N/A | SCA Pole Mounted Sub |  |  | 0.1887 | 9.9047
D.F.ZN09035/00001R | D.F.ZN09035/000001 | 0 | Sutherland | CARINGBAH |  | 370 | 3.124 | 163.968
D.F.ZN09035/00001L | D.F.ZN09035/000001 | 1 | Sutherland | CARINGBAH |  | 330 | 0.5912 | 31.0319
D.F.ZN09035/000002 | D.F.ZN09035/000002 | 0 | Sutherland | CARINGBAH |  | 285 | 2.1069 | 110.5813
D.F.ZN09035/00004R | D.F.ZN09035/000004 | 0 | Sutherland | CARINGBAH |  | 315 | 4.2967 | 225.517
D.F.ZN09035/00004L | D.F.ZN09035/000004 | 1 | Sutherland | CARINGBAH |  | 330 | 2.7981 | 146.8635
D.F.ZN09035/00005L | D.F.ZN09035/000005 | 0 | Sutherland | CARINGBAH |  | 330 | 0.8297 | 43.5501
D.F.ZN09035/00005R | D.F.ZN09035/000005 | 1 | Sutherland | CARINGBAH |  | 395 | 0.9308 | 48.8531
D.F.ZN09035/00007R | D.F.ZN09035/000007 | 0 | Sutherland | CARINGBAH |  | 315 | 2.1682 | 113.7984
D.F.ZN09035/00007L | D.F.ZN09035/000007 | 1 | Sutherland | CARINGBAH |  | 350 | 0.8968 | 47.0718
D.F.ZN09035/000008 | D.F.ZN09035/000008 | 0 | Sutherland | CARINGBAH |  | 340 | 2.3029 | 120.87
D.F.ZN09035/000010 | D.F.ZN09035/000010 | 0 | Sutherland | CARINGBAH |  | 400 | 1.9452 | 102.095
D.F.ZN09035/00011R | D.F.ZN09035/000011 | 0 | Sutherland | CARINGBAH |  | 400 | 4.0509 | 212.6186
D.F.ZN09035/00011L | D.F.ZN09035/000011 | 1 | Sutherland | CARINGBAH |  | 340 |  | 0
D.F.ZN09037/000002 | D.F.ZN09037/000002 | 0 | Sutherland | MIRANDA |  | 335 | 2.8605 | 150.135
D.F.ZN09037/000003 | D.F.ZN09037/000003 | 0 | Sutherland | MIRANDA |  | 360 | 2.0054 | 105.2585
D.F.ZN09037/000004 | D.F.ZN09037/000004 | 0 | Sutherland | MIRANDA |  | 400 | 3.6724 | 192.7509
D.F.ZN09037/000007 | D.F.ZN09037/000007 | 0 | Sutherland | MIRANDA |  | 330 | 2.2913 | 120.2614
D.F.ZN09037/000008 | D.F.ZN09037/000008 | 0 | Sutherland | MIRANDA |  | 400 | 4.2882 | 225.0744
D.F.ZN09037/000009 | D.F.ZN09037/000009 | 0 | Sutherland | MIRANDA |  | 400 | 2.2284 | 116.9588
D.F.ZN09037/000010 | D.F.ZN09037/000010 | 0 | Sutherland | MIRANDA |  | 335 | 3.0679 | 161.0227
D.F.ZN09037/000014 | D.F.ZN09037/000014 | 0 | Sutherland | MIRANDA |  | 360 | 2.635 | 138.3008
D.F.ZN09037/000015 | D.F.ZN09037/000015 | 0 | Sutherland | MIRANDA |  | 400 | 3.5671 | 187.2244
D.F.ZN09037/000016 | D.F.ZN09037/000016 | 0 | Sutherland | MIRANDA |  | 395 | 3.2793 | 172.1191
D.F.ZN09037/000017 | D.F.ZN09037/000017 | 0 | Sutherland | MIRANDA |  | 400 | 4.0979 | 215.0862
D.F.ZN09118/000002 | D.F.ZN09118/000002 | 0 | Sutherland | CRONULLA |  | 385 | 1.8423 | 96.6974
D.F.ZN09118/000003 | D.F.ZN09118/000003 | 0 | Sutherland | CRONULLA |  | 400 | 1.8547 | 97.3489
D.F.ZN09118/000004 | D.F.ZN09118/000004 | 0 | Sutherland | CRONULLA |  | 340 | 2.0726 | 108.7821
D.F.ZN09118/000006 | D.F.ZN09118/000006 | 0 | Sutherland | CRONULLA |  | 330 | 3.9844 | 209.1269
D.F.ZN09118/000007 | D.F.ZN09118/000007 | 0 | Sutherland | CRONULLA |  | 400 | 3.2863 | 172.4864
D.F.ZN09118/000008 | D.F.ZN09118/000008 | 0 | Sutherland | CRONULLA |  | 400 | 3.5669 | 187.2126
D.F.ZN09118/000011 | D.F.ZN09118/000011 | 0 | Sutherland | CRONULLA |  | 400 | 3.8347 | 201.2718
D.F.ZN09118/000012 | D.F.ZN09118/000012 | 0 | Sutherland | CRONULLA |  | 340 | 3.6002 | 188.9637
D.F.ZN09118/000013 | D.F.ZN09118/000013 | 0 | Sutherland | CRONULLA |  | 340 | 2.566 | 134.6804
D.F.ZN09118/000015 | D.F.ZN09118/000015 | 0 | Sutherland | CRONULLA |  | 400 | 4.4311 | 232.5743
D.F.ZN09118/000016 | D.F.ZN09118/000016 | 0 | Sutherland | CRONULLA |  | 320 | 2.3388 | 122.756
D.F.ZN09118/000017 | D.F.ZN09118/000017 | 0 | Sutherland | CRONULLA |  | 340 | 2.9297 | 153.7682
D.F.ZN09118/000020 | D.F.ZN09118/000020 | 0 | Sutherland | CRONULLA |  | 315 | 4.1419 | 217.3948
D.F.ZN09118/000021 | D.F.ZN09118/000021 | 0 | Sutherland | CRONULLA |  | 400 | 3.4304 | 180.0482
D.F.ZN09118/000022 | D.F.ZN09118/000022 | 0 | Sutherland | CRONULLA |  | 400 | 1.7387 | 91.2601
D.F.ZN09118/000024 | D.F.ZN09118/000024 | 0 | Sutherland | CRONULLA |  | 360 | 2.3272 | 122.1466
D.F.ZN09118/000025 | D.F.ZN09118/000025 | 0 | Sutherland | CRONULLA |  | 400 | 1.93 | 101.2979
D.F.ZN09118/000026 | D.F.ZN09118/000026 | 0 | Sutherland | CRONULLA |  | 360 | 4.3163 | 226.5469
D.F.ZN09171/000004 | D.F.ZN09171/000004 | 0 | Sutherland | LUCAS HEIGHTS |  | 265 | 0.5594 | 29.3622
D.F.ZN09171/000005 | D.F.ZN09171/000005 | 0 | Sutherland | LUCAS HEIGHTS |  | 265 |  | 0
D.F.ZN09171/000007 | D.F.ZN09171/000007 | 0 | Sutherland | LUCAS HEIGHTS |  | 400 | 3.5424 | 185.9278
D.F.ZN09171/000013 | D.F.ZN09171/000013 | 0 | Sutherland | LUCAS HEIGHTS |  | 400 | 4.1712 | 218.9312
D.F.ZN09245/00001L | D.F.ZN09245/000001 | 0 | Sutherland | ENGADINE |  | 400 | 2.7652 | 145.1343
D.F.ZN09245/000003 | D.F.ZN09245/000003 | 0 | Sutherland | ENGADINE |  | 320 | 2.9785 | 156.3291
D.F.ZN09245/000004 | D.F.ZN09245/000004 | 0 | Sutherland | ENGADINE |  | 360 | 2.4264 | 127.3531
D.F.ZN09245/00006L | D.F.ZN09245/000006 | 0 | Sutherland | ENGADINE |  | 320 | 0.688 | 36.1089
D.F.ZN09245/000009 | D.F.ZN09245/000009 | 0 | Sutherland | ENGADINE |  | 340 | 1.5966 | 83.8018
D.F.ZN09245/000010 | D.F.ZN09245/000010 | 0 | Sutherland | ENGADINE |  | 350 | 3.5066 | 184.0476
D.F.ZN09245/000013 | D.F.ZN09245/000013 | 0 | Sutherland | ENGADINE |  | 355 | 3.4522 | 181.1942
D.F.ZN09245/00015L | D.F.ZN09245/000015 | 0 | Sutherland | ENGADINE |  | 340 | 3.6356 | 190.8182
D.F.ZN09245/000019 | D.F.ZN09245/000019 | 0 | Sutherland | ENGADINE |  | 400 | 3.6122 | 189.5896
D.F.ZN09245/00021L | D.F.ZN09245/000021 | 0 | Sutherland | ENGADINE |  | 400 | 2.6262 | 137.8422
D.F.ZN09252/000021 | D.F.ZN09252/000021 | 0 | Sutherland | JANNALI |  | 340 | 2.1751 | 114.1615
D.F.ZN09252/000022 | D.F.ZN09252/000022 | 0 | Sutherland | JANNALI |  | 400 | 3.1 | 162.7095
D.F.ZN09252/00024L | D.F.ZN09252/000024 | 0 | Sutherland | JANNALI |  | 385 |  | 0
D.F.ZN09252/00024R | D.F.ZN09252/000024 | 1 | Sutherland | JANNALI |  | 340 |  | 0
D.F.ZN09252/000025 | D.F.ZN09252/000025 | 0 | Sutherland | JANNALI |  | 315 | 2.3079 | 121.1342
D.F.ZN09252/000027 | D.F.ZN09252/000027 | 0 | Sutherland | JANNALI |  | 400 | 4.0535 | 212.7546
D.F.ZN09252/00028L | D.F.ZN09252/000028 | 0 | Sutherland | JANNALI |  | 315 |  | 0
D.F.ZN09252/00028R | D.F.ZN09252/000028 | 1 | Sutherland | JANNALI |  | 325 |  | 0
D.F.ZN09252/00030L | D.F.ZN09252/000030 | 0 | Sutherland | JANNALI |  | 315 |  | 0
D.F.ZN09252/00030R | D.F.ZN09252/000030 | 1 | Sutherland | JANNALI |  | 345 |  | 0
D.F.ZN09252/00031L | D.F.ZN09252/000031 | 0 | Sutherland | JANNALI |  | 400 |  | 0
D.F.ZN09252/00031R | D.F.ZN09252/000031 | 1 | Sutherland | JANNALI |  | 305 |  | 0
D.F.ZN09534/000003 | D.F.ZN09534/000003 | 0 | Sutherland | KURNELL SOUTH |  | 300 | 1.1536 | 60.5483
D.F.ZN09534/000006 | D.F.ZN09534/000006 | 0 | Sutherland | KURNELL SOUTH |  | 300 | 1.4384 | 75.4964
D.F.ZN09534/000007 | D.F.ZN09534/000007 | 0 | Sutherland | KURNELL SOUTH |  | 300 | 0 | 0
D.F.ZN09534/00010L | D.F.ZN09534/000010 | 0 | Sutherland | KURNELL SOUTH |  | 310 | 0.0423 | 2.2187
D.F.ZN09534/000011 | D.F.ZN09534/000011 | 0 | Sutherland | KURNELL SOUTH |  | 160 | 0.6155 | 32.3056
D.F.ZN09534/000012 | D.F.ZN09534/000012 | 0 | Sutherland | KURNELL SOUTH |  | 400 | 0.232 | 12.1747
D.F.ZN09534/00015L | D.F.ZN09534/000015 | 0 | Sutherland | KURNELL SOUTH |  | 375 | 0.8465 | 44.4304
D.F.ZN09534/000017 | D.F.ZN09534/000017 | 0 | Sutherland | KURNELL SOUTH |  | 375 | 1.8125 | 95.1309
D.F.ZN09534/000018 | D.F.ZN09534/000018 | 0 | Sutherland | KURNELL SOUTH |  | 400 | 1.8142 | 95.2228
D.F.ZN09534/000019 | D.F.ZN09534/000019 | 0 | Sutherland | KURNELL SOUTH |  | 300 | 0.9663 | 50.7155
D.F.ZN09550/000001 | D.F.ZN09550/000001 | 0 | Sutherland | GWAWLEY BAY |  | 400 | 2.3434 | 122.9966
D.F.ZN09550/000003 | D.F.ZN09550/000003 | 0 | Sutherland | GWAWLEY BAY |  | 390 | 2.6695 | 140.1139
D.F.ZN09550/00004L | D.F.ZN09550/000004 | 0 | Sutherland | GWAWLEY BAY |  | 400 | 0.9324 | 48.9375
D.F.ZN09550/000006 | D.F.ZN09550/000006 | 0 | Sutherland | GWAWLEY BAY |  | 390 | 2.47 | 129.6418
D.F.ZN09550/00008L | D.F.ZN09550/000008 | 0 | Sutherland | GWAWLEY BAY |  |  |  | 0
D.F.ZN09550/000009 | D.F.ZN09550/000009 | 0 | Sutherland | GWAWLEY BAY |  | 340 | 1.7008 | 89.2679
D.F.ZN09550/000011 | D.F.ZN09550/000011 | 0 | Sutherland | GWAWLEY BAY |  | 400 | 3.2019 | 168.0561
D.F.ZN09550/000027 | D.F.ZN09550/000027 | 0 | Sutherland | GWAWLEY BAY |  | 310 | 2.0219 | 106.1206
D.F.ZN09550/000028 | D.F.ZN09550/000028 | 0 | Sutherland | GWAWLEY BAY |  | 390 | 1.9172 | 100.6289
D.F.ZN09550/000033 | D.F.ZN09550/000033 | 0 | Sutherland | GWAWLEY BAY |  | 285 | 1.9761 | 103.7198
D.F.ZN09550/000034 | D.F.ZN09550/000034 | 0 |  | GWAWLEY BAY |  |  |  | 0
D.F.ZN09550/000036 | D.F.ZN09550/000036 | 0 | Sutherland | GWAWLEY BAY |  | 305 | 1.9966 | 104.7937
D.F.ZN09550/000041 | D.F.ZN09550/000041 | 0 | Sutherland | GWAWLEY BAY |  | 400 | 2.0534 | 107.7732
D.F.ZN09550/000042 | D.F.ZN09550/000042 | 0 | Sutherland | GWAWLEY BAY |  | 365 | 2.5986 | 136.3936
D.F.ZN09550/000043 | D.F.ZN09550/000043 | 0 | Sutherland | GWAWLEY BAY |  | 400 | 3.5 | 183.7027
D.F.ZN09700/000011 | D.F.ZN09700/000011 | 0 | Sutherland | KIRRAWEE |  | 365 | 3.4337 | 180.2199
D.F.ZN09700/000012 | D.F.ZN09700/000012 | 0 | Sutherland | KIRRAWEE |  | 390 | 4.5661 | 239.6565
D.F.ZN09700/000015 | D.F.ZN09700/000015 | 0 | Sutherland | KIRRAWEE |  | 340 | 2.9936 | 157.1245
D.F.ZN09700/000016 | D.F.ZN09700/000016 | 0 | Sutherland | KIRRAWEE |  | 390 | 4.1932 | 220.0867
D.F.ZN09700/000017 | D.F.ZN09700/000017 | 0 | Sutherland | KIRRAWEE |  | 400 | 2.9314 | 153.859
D.F.ZN09700/000018 | D.F.ZN09700/000018 | 0 | Sutherland | KIRRAWEE |  | 365 | 4.4769 | 234.9739
D.F.ZN09700/000019 | D.F.ZN09700/000019 | 0 | Sutherland | KIRRAWEE |  | 385 | 2.4283 | 127.4548
D.F.ZN09700/000020 | D.F.ZN09700/000020 | 0 | Sutherland | KIRRAWEE |  | 400 | 2.3364 | 122.6295
D.F.ZN09700/000021 | D.F.ZN09700/000021 | 0 | Sutherland | KIRRAWEE |  | 340 | 3.063 | 160.7668
D.F.ZN09700/000022 | D.F.ZN09700/000022 | 0 | Sutherland | KIRRAWEE |  | 400 | 2.3945 | 125.6769
D.F.ZN09700/000023 | D.F.ZN09700/000023 | 0 | Sutherland | KIRRAWEE |  | 400 | 3.6188 | 189.9399
D.F.ZN09700/000024 | D.F.ZN09700/000024 | 0 | Sutherland | KIRRAWEE |  | 390 | 3.977 | 208.7391
D.F.ZN09900/00001L | D.F.ZN09900/000001 | 0 | Sutherland | MENAI |  | 325 | 2.2776 | 119.543
D.F.ZN09900/00001R | D.F.ZN09900/000001 | 1 | Sutherland | MENAI |  | 370 | 1.9025 | 99.8537
D.F.ZN09900/000002 | D.F.ZN09900/000002 | 0 | Sutherland | MENAI |  | 400 | 1.9666 | 103.2214
D.F.ZN09900/000003 | D.F.ZN09900/000003 | 0 | Sutherland | MENAI |  | 320 | 2.337 | 122.6592
D.F.ZN09900/000005 | D.F.ZN09900/000005 | 0 | Sutherland | MENAI |  | 325 | 1.2591 | 66.0841
D.F.ZN09900/000006 | D.F.ZN09900/000006 | 0 | Sutherland | MENAI |  | 325 | 2.0386 | 107.0001
D.F.ZN09900/000008 | D.F.ZN09900/000008 | 0 | Sutherland | MENAI |  | 350 | 3.0197 | 158.4926
D.F.ZN09900/000009 | D.F.ZN09900/000009 | 0 | Sutherland | MENAI |  | 325 | 1.5252 | 80.0533
D.F.ZN09900/000010 | D.F.ZN09900/000010 | 0 | Sutherland | MENAI |  | 400 | 1.6816 | 88.2636
D.F.ZN09900/000012 | D.F.ZN09900/000012 | 0 | Sutherland | MENAI |  | 295 | 3.3565 | 176.1729
D.F.ZN09900/000013 | D.F.ZN09900/000013 | 0 | Sutherland | MENAI |  | 400 | 2.1729 | 114.0498
D.F.ZN09900/000014 | D.F.ZN09900/000014 | 0 | Sutherland | MENAI |  | 325 | 2.0452 | 107.3426
D.F.ZN09900/000016 | D.F.ZN09900/000016 | 0 | Sutherland | MENAI |  | 325 | 0.57 | 29.9149
D.F.ZN09900/000017 | D.F.ZN09900/000017 | 0 | Sutherland | MENAI |  | 370 | 2.7659 | 145.1744
D.F.ZN09900/000019 | D.F.ZN09900/000019 | 0 | Sutherland | MENAI |  | 370 | 2.2259 | 116.8279
D.F.ZN09900/000020 | D.F.ZN09900/000020 | 0 | Sutherland | MENAI |  | 325 | 1.2439 | 65.2895
D.F.ZN09900/000021 | D.F.ZN09900/000021 | 0 | Sutherland | MENAI |  | 325 | 1.9779 | 103.8137
D.F.ZN10991/000001 | D.F.ZN10991/000001 | 0 | St George | BLAKEHURST |  | 355 | 3.5411 | 185.861 | 1
D.F.ZN10991/000002 | D.F.ZN10991/000002 | 0 | St George | BLAKEHURST |  | 355 | 1.5649 | 82.1372
D.F.ZN10991/000005 | D.F.ZN10991/000005 | 0 | St George | BLAKEHURST |  | 355 | 1.7946 | 94.1921
D.F.ZN10991/000006 | D.F.ZN10991/000006 | 0 | St George | BLAKEHURST |  | 315 | 1.9669 | 103.2336
D.F.ZN10991/000007 | D.F.ZN10991/000007 | 0 | St George | BLAKEHURST |  | 355 | 2.4058 | 126.2742
D.F.ZN10991/000008 | D.F.ZN10991/000008 | 0 | St George | BLAKEHURST |  | 300 | 3.6954 | 193.9561
D.F.ZN10991/000012 | D.F.ZN10991/000012 | 0 | St George | BLAKEHURST |  | 355 | 3.4144 | 179.2104 | 1
D.F.ZN10991/000013 | D.F.ZN10991/000013 | 0 | St George | BLAKEHURST |  | 305 | 2.3211 | 121.8252
D.F.ZN10993/00022L | D.F.ZN10993/000022 | 0 | St George | HURSTVILLE NORTH |  | 400 | 2.2469 | 117.9312
D.F.ZN10993/000023 | D.F.ZN10993/000023 | 0 | St George | HURSTVILLE NORTH |  | 395 | 3.5766 | 187.7207
D.F.ZN10993/000026 | D.F.ZN10993/000026 | 0 | St George | HURSTVILLE NORTH |  | 280 | 2.1985 | 115.39
D.F.ZN10993/00027L | D.F.ZN10993/000027 | 0 | St George | HURSTVILLE NORTH |  | 400 | 1.8285 | 95.973
D.F.ZN10993/000033 | D.F.ZN10993/000033 | 0 | St George | HURSTVILLE NORTH |  | 285 | 2.9563 | 155.1646
D.F.ZN10993/00034L | D.F.ZN10993/000034 | 0 | St George | HURSTVILLE NORTH |  | 280 | 2.701 | 141.7665
D.F.ZN10993/000035 | D.F.ZN10993/000035 | 0 | St George | HURSTVILLE NORTH |  | 395 | 2.2814 | 119.7449
D.F.ZN10993/00039L | D.F.ZN10993/000039 | 0 | St George | HURSTVILLE NORTH |  | 400 | 1.9548 | 102.5988
D.F.ZN10993/000043 | D.F.ZN10993/000043 | 0 | St George | HURSTVILLE NORTH |  | 395 | 2.0204 | 106.0413
D.F.ZN10994/000001 | D.F.ZN10994/000001 | 0 | St George | MORTDALE |  | 400 | 2.3124 | 121.3696
D.F.ZN10994/00002L | D.F.ZN10994/000002 | 0 | St George | MORTDALE |  | 400 | 3.2344 | 169.7632
D.F.ZN10994/000003 | D.F.ZN10994/000003 | 0 | St George | MORTDALE |  | 370 | 2.1038 | 110.4214
D.F.ZN10994/00004L | D.F.ZN10994/000004 | 0 | St George | MORTDALE |  | 400 | 3.9591 | 207.7975
D.F.ZN10994/000007 | D.F.ZN10994/000007 | 0 | St George | MORTDALE |  | 335 | 3.6434 | 191.2288
D.F.ZN10994/00008L | D.F.ZN10994/000008 | 0 | St George | MORTDALE |  | 330 | 0.9786 | 51.3624
D.F.ZN10994/000009 | D.F.ZN10994/000009 | 0 | St George | MORTDALE |  | 315 | 1.5576 | 81.7539
D.F.ZN10994/00010L | D.F.ZN10994/000010 | 0 | St George | MORTDALE |  | 395 | 2.5052 | 131.491
D.F.ZN10994/000011 | D.F.ZN10994/000011 | 0 | St George | MORTDALE |  | 305 | 2.0649 | 108.3771
D.F.ZN10994/00012L | D.F.ZN10994/000012 | 0 | St George | MORTDALE |  | 400 | 3.8372 | 201.401
D.F.ZN10994/000013 | D.F.ZN10994/000013 | 0 | St George | MORTDALE |  | 400 | 2.2102 | 116.0032
D.F.ZN10994/00014L | D.F.ZN10994/000014 | 0 | St George | MORTDALE |  | 400 | 1.6599 | 87.1216
D.F.ZN10994/000018 | D.F.ZN10994/000018 | 0 | St George | MORTDALE |  | 340 | 1.551 | 81.4069
D.F.ZN10994/00019L | D.F.ZN10994/000019 | 0 | St George | MORTDALE |  | 370 | 3.2146 | 168.7235
D.F.ZN10994/000020 | D.F.ZN10994/000020 | 0 | St George | MORTDALE |  | 305 | 2.7281 | 143.1871
D.F.ZN10994/00021L | D.F.ZN10994/000021 | 0 | St George | MORTDALE |  | 330 | 2.2113 | 116.064
D.F.ZN10995/000001 | D.F.ZN10995/000001 | 0 | St George | RIVERWOOD |  | 365 | 3.5152 | 184.502
D.F.ZN10995/000002 | D.F.ZN10995/000002 | 0 | St George | RIVERWOOD |  | 400 | 4.5983 | 241.3501
D.F.ZN10995/000005 | D.F.ZN10995/000005 | 0 | St George | RIVERWOOD |  | 340 | 3.5523 | 186.4473
D.F.ZN10995/000006 | D.F.ZN10995/000006 | 0 | St George | RIVERWOOD |  | 350 | 2.9258 | 153.5667
D.F.ZN10995/000007 | D.F.ZN10995/000007 | 0 | St George | RIVERWOOD |  | 355 | 3.1872 | 167.2863
D.F.ZN10995/000008 | D.F.ZN10995/000008 | 0 | St George | RIVERWOOD |  | 385 | 3.3203 | 174.268
D.F.ZN10995/000012 | D.F.ZN10995/000012 | 0 | St George | RIVERWOOD |  | 315 | 2.7289 | 143.2287
D.F.ZN10995/000013 | D.F.ZN10995/000013 | 0 | St George | RIVERWOOD |  | 385 | 2.9917 | 157.0234
D.F.ZN10997/000001 | D.F.ZN10997/000001 | 0 | St George | SANS SOUCI |  | 380 | 1.7193 | 90.2407
D.F.ZN10997/000002 | D.F.ZN10997/000002 | 0 | St George | SANS SOUCI |  | 295 | 3.6394 | 191.0171
D.F.ZN10997/000005 | D.F.ZN10997/000005 | 0 | St George | SANS SOUCI |  | 330 | 1.5074 | 79.1162
D.F.ZN10997/000006 | D.F.ZN10997/000006 | 0 | St George | SANS SOUCI |  | 400 | 0.7437 | 39.0366
D.F.ZN10997/000007 | D.F.ZN10997/000007 | 0 | St George | SANS SOUCI |  | 305 | 2.2894 | 120.1647
D.F.ZN10997/000008 | D.F.ZN10997/000008 | 0 | St George | SANS SOUCI |  | 400 | 0.4524 | 23.7459
D.F.ZN10997/000011 | D.F.ZN10997/000011 | 0 | St George | SANS SOUCI |  | 315 | 2.4301 | 127.5476
D.F.ZN10997/000012 | D.F.ZN10997/000012 | 0 | St George | SANS SOUCI |  | 255 | 2.6345 | 138.2767
D.F.ZN10998/000001 | D.F.ZN10998/000001 | 0 | St George | ROCKDALE |  | 400 | 2.7188 | 142.6986
D.F.ZN10998/000002 | D.F.ZN10998/000002 | 0 | St George | ROCKDALE |  | 220 | 1.7795 | 93.3984
D.F.ZN10998/000003 | D.F.ZN10998/000003 | 0 | St George | ROCKDALE |  | 345 | 2.1294 | 111.7642
D.F.ZN10998/000005 | D.F.ZN10998/000005 | 0 | St George | ROCKDALE |  | 330 | 0.9345 | 49.0463
D.F.ZN10998/000008 | D.F.ZN10998/000008 | 0 | St George | ROCKDALE |  | 340 | 3.2967 | 173.0296
D.F.ZN10998/000009 | D.F.ZN10998/000009 | 0 | St George | ROCKDALE |  | 360 | 4.2325 | 222.1469
D.F.ZN10998/000010 | D.F.ZN10998/000010 | 0 | St George | ROCKDALE |  | 330 | 3.5803 | 187.9154
D.F.ZN10998/000012 | D.F.ZN10998/000012 | 0 | St George | ROCKDALE |  | 400 | 0.537 | 28.1852
D.F.ZN10998/000013 | D.F.ZN10998/000013 | 0 | St George | ROCKDALE |  | 400 | 2.9745 | 156.1195
D.F.ZN10998/000015 | D.F.ZN10998/000015 | 0 | St George | ROCKDALE |  | 400 | 5.2778 | 277.0127
D.F.ZN10998/000016 | D.F.ZN10998/000016 | 0 | St George | ROCKDALE |  | 400 | 2.8913 | 151.756
D.F.ZN10998/000017 | D.F.ZN10998/000017 | 0 | St George | ROCKDALE |  | 395 | 3.1903 | 167.4474
D.F.ZN10998/000018 | D.F.ZN10998/000018 | 0 | St George | ROCKDALE |  | 400 | 2.4954 | 130.9721
D.F.ZN10998/000019 | D.F.ZN10998/000019 | 0 | St George | ROCKDALE |  | 370 | 1.7834 | 93.6054
D.F.ZN10998/000024 | D.F.ZN10998/000024 | 0 | St George | ROCKDALE |  | 310 | 1.2359 | 64.8665
D.F.ZN10998/000025 | D.F.ZN10998/000025 | 0 | St George | ROCKDALE |  | 305 | 1.061 | 55.6879
D.F.ZN10998/000026 | D.F.ZN10998/000026 | 0 | St George | ROCKDALE |  | 400 | 1.9876 | 104.3241
D.F.ZN10998/000028 | D.F.ZN10998/000028 | 0 | St George | ROCKDALE |  | 360 | 2.1105 | 110.772
D.F.ZN10998/000029 | D.F.ZN10998/000029 | 0 | St George | ROCKDALE |  | 400 | 2.67 | 140.1392
D.F.ZN10998/000031 | D.F.ZN10998/000031 | 0 | St George | ROCKDALE |  | 315 | 2.7068 | 142.0708
D.F.ZN10998/000032 | D.F.ZN10998/000032 | 0 | St George | ROCKDALE |  | 400 | 3.5047 | 183.9475
D.F.ZN10999/00001L | D.F.ZN10999/000001 | 0 | St George | KOGARAH |  | 400 | 1.4776 | 77.5537
D.F.ZN10999/000002 | D.F.ZN10999/000002 | 0 | St George | KOGARAH |  | 400 | 1.2283 | 64.4709
D.F.ZN10999/00003L | D.F.ZN10999/000003 | 0 | St George | KOGARAH |  | 400 | 3.6513 | 191.6415
D.F.ZN10999/000004 | D.F.ZN10999/000004 | 0 | St George | KOGARAH |  | 315 | 3.091 | 162.2334
D.F.ZN10999/000007 | D.F.ZN10999/000007 | 0 | St George | KOGARAH |  | 260 | 2.6285 | 137.9613
D.F.ZN10999/00009L | D.F.ZN10999/000009 | 0 | St George | KOGARAH |  | 400 | 1.4587 | 76.5595
D.F.ZN10999/000010 | D.F.ZN10999/000010 | 0 | St George | KOGARAH |  | 400 | 3.9675 | 208.2421
D.F.ZN10999/00011L | D.F.ZN10999/000011 | 0 | St George | KOGARAH |  | 385 | 2.7281 | 143.1863
D.F.ZN10999/00012L | D.F.ZN10999/000012 | 0 | St George | KOGARAH |  | 395 | 4.618 | 242.3828
D.F.ZN10999/00014L | D.F.ZN10999/000014 | 0 | St George | KOGARAH |  | 300 | 4.7498 | 249.3007
D.F.ZN10999/000015 | D.F.ZN10999/000015 | 0 | St George | KOGARAH |  | 335 | 2.5407 | 133.3526
D.F.ZN10999/00016L | D.F.ZN10999/000016 | 0 | St George | KOGARAH |  | 400 | 3.0972 | 162.5614
D.F.ZN10999/000017 | D.F.ZN10999/000017 | 0 | St George | KOGARAH |  | 300 | 2.6873 | 141.0491
D.F.ZN10999/00019L | D.F.ZN10999/000019 | 0 | St George | KOGARAH |  | 400 | 3.5816 | 187.9872
D.F.ZN10999/00022L | D.F.ZN10999/000022 | 0 | St George | KOGARAH |  | 315 | 3.3446 | 175.5464
D.F.ZN10999/000023 | D.F.ZN10999/000023 | 0 | St George | KOGARAH |  | 400 | 3.257 | 170.9498
D.F.ZN10999/00024L | D.F.ZN10999/000024 | 0 | St George | KOGARAH |  | 260 | 1.6322 | 85.6661
D.F.ZN10999/00025L | D.F.ZN10999/000025 | 0 | St George | KOGARAH |  | 295 | 2.4667 | 129.4679
D.F.ZN10999/00028L | D.F.ZN10999/000028 | 0 | St George | KOGARAH |  | 305 | 2.7557 | 144.6361
D.F.ZN10999/000029 | D.F.ZN10999/000029 | 0 | St George | KOGARAH |  | 300 | 3.0173 | 158.3697
D.F.ZN10999/00030L | D.F.ZN10999/000030 | 0 | St George | KOGARAH |  | 385 | 0.4138 | 21.7175
D.F.ZN10999/000032 | D.F.ZN10999/000032 | 0 | St George | KOGARAH |  | 270 | 3.3513 | 175.8987
D.F.ZN10999/000035 | D.F.ZN10999/000035 | 0 | St George | KOGARAH |  | 295 | 2.6334 | 138.217
D.F.ZN10999/00036L | D.F.ZN10999/000036 | 0 | St George | KOGARAH |  | 260 | 1.5746 | 82.6434
D.F.ZN10999/000037 | D.F.ZN10999/000037 | 0 | St George | KOGARAH |  | 355 | 1.8362 | 96.3766
D.F.ZN10999/00038L | D.F.ZN10999/000038 | 0 | St George | KOGARAH |  | 400 | 2.5589 | 134.3074
D.F.ZN10999/00039L | D.F.ZN10999/000039 | 0 | St George | KOGARAH |  | 400 | 2.5349 | 133.0492
D.F.ZN12570/00021L | D.F.ZN12570/000021 | 0 | Lower Central Coast | AVOCA |  | 400 | 2.6251 | 137.784
D.F.ZN12570/00021R | D.F.ZN12570/000021 | 1 | Lower Central Coast | AVOCA |  |  |  | 0
D.F.ZN12570/000022 | D.F.ZN12570/000022 | 0 | Lower Central Coast | AVOCA |  | 400 | 3.5986 | 188.8773
D.F.ZN12570/000024 | D.F.ZN12570/000024 | 0 | Lower Central Coast | AVOCA |  | 280 | 3.0051 | 157.7272
D.F.ZN12570/000025 | D.F.ZN12570/000025 | 0 | Lower Central Coast | AVOCA |  | 375 | 1.6581 | 87.0299
D.F.ZN12570/000026 | D.F.ZN12570/000026 | 0 | Lower Central Coast | AVOCA |  | 400 | 4.0838 | 214.3453
D.F.ZN12570/00028R | D.F.ZN12570/000028 | 0 | Lower Central Coast | AVOCA |  |  |  | 0
D.F.ZN12570/000029 | D.F.ZN12570/000029 | 0 | Lower Central Coast | AVOCA |  | 280 | 1.6298 | 85.5401
D.F.ZN12570/00030 | D.F.ZN12570/000030 | 0 | Lower Central Coast | AVOCA |  |  |  | 0
D.F.ZN12570/00032R | D.F.ZN12570/000032 | 0 | Lower Central Coast | AVOCA |  |  |  | 0
D.F.ZN12570/000033 | D.F.ZN12570/000033 | 0 | Lower Central Coast | AVOCA |  | 325 | 2.9687 | 155.8142
D.F.ZN12570/000034 | D.F.ZN12570/000034 | 0 | Lower Central Coast | AVOCA |  | 295 | 1.8911 | 99.2573
D.F.ZN12570/000035 | D.F.ZN12570/000035 | 0 | Lower Central Coast | AVOCA |  | 400 | 3.5285 | 185.2
D.F.ZN12570/00037L | D.F.ZN12570/000037 | 0 | Lower Central Coast | AVOCA |  | 320 | 3.3306 | 174.8112
D.F.ZN12570/00037R | D.F.ZN12570/000037 | 1 | Lower Central Coast | AVOCA |  |  |  | 0
D.F.ZN12570/000039 | D.F.ZN12570/000039 | 0 | Lower Central Coast | AVOCA |  | 295 | 3.1491 | 165.2853
D.F.ZN12570/000040 | D.F.ZN12570/000040 | 0 | Lower Central Coast | AVOCA |  | 400 | 2.768 | 145.2814
D.F.ZN12570/000041 | D.F.ZN12570/000041 | 0 | Lower Central Coast | AVOCA |  | 295 | 1.803 | 94.6322
D.F.ZN12580/000001 | D.F.ZN12580/000001 | 0 | Lower Central Coast | ERINA |  | 400 | 3.7228 | 195.3964
D.F.ZN12580/000002 | D.F.ZN12580/000002 | 0 | Lower Central Coast | ERINA |  | 400 | 2.089 | 109.6426
D.F.ZN12580/00004L | D.F.ZN12580/000004 | 0 | Lower Central Coast | ERINA |  | 400 | 3.3932 | 178.0947
D.F.ZN12580/00004R | D.F.ZN12580/000004 | 1 | Lower Central Coast | ERINA |  | 280 | 1.1091 | 58.215
D.F.ZN12580/000007 | D.F.ZN12580/000007 | 0 | Lower Central Coast | ERINA |  | 400 | 5.0624 | 265.7068
D.F.ZN12580/000008 | D.F.ZN12580/000008 | 0 | Lower Central Coast | ERINA |  | 400 | 3.9969 | 209.7852
D.F.ZN12580/000010 | D.F.ZN12580/000010 | 0 | Lower Central Coast | ERINA |  | 320 | 3.9502 | 207.3342
D.F.ZN12580/00012R | D.F.ZN12580/000012 | 0 | Lower Central Coast | ERINA |  | 350 | 3.497 | 183.5424
D.F.ZN12580/00012L | D.F.ZN12580/000012 | 1 | Lower Central Coast | ERINA |  | 310 | 1.2876 | 67.5789
D.F.ZN12580/000013 | D.F.ZN12580/000013 | 0 | Lower Central Coast | ERINA |  | 280 |  | 0
D.F.ZN12580/000014 | D.F.ZN12580/000014 | 0 | Lower Central Coast | ERINA |  | 280 | 3.7047 | 194.4465
D.F.ZN12580/00016L | D.F.ZN12580/000016 | 0 | Lower Central Coast | ERINA |  | 305 | 3.2299 | 169.5233
D.F.ZN12580/00016R | D.F.ZN12580/000016 | 1 | Lower Central Coast | ERINA |  | 255 | 0.428 | 22.4654
D.F.ZN12600/000001 | D.F.ZN12600/000001 | 0 | Lower Central Coast | LISAROW |  | 305 | 1.8443 | 96.8027
D.F.ZN12600/000002 | D.F.ZN12600/000002 | 0 | Lower Central Coast | LISAROW |  | 320 | 4.4398 | 233.0271
D.F.ZN12600/000003 | D.F.ZN12600/000003 | 0 | Lower Central Coast | LISAROW |  | 305 | 3.443 | 180.7107
D.F.ZN12600/000005 | D.F.ZN12600/000005 | 0 | Lower Central Coast | LISAROW |  | 305 | 2.2044 | 115.7017
D.F.ZN12600/000009 | D.F.ZN12600/000009 | 0 | Lower Central Coast | LISAROW |  | 325 | 3.1595 | 165.831
D.F.ZN12600/000011 | D.F.ZN12600/000011 | 0 | Lower Central Coast | LISAROW |  | 325 | 2.9672 | 155.7393
D.F.ZN12600/000012 | D.F.ZN12600/000012 | 0 | Lower Central Coast | LISAROW |  | 370 | 2.6407 | 138.6023
D.F.ZN12600/000013 | D.F.ZN12600/000013 | 0 | Lower Central Coast | LISAROW |  | 305 | 2.382 | 125.0202
D.F.ZN12610/000002 | D.F.ZN12610/000002 | 0 | Lower Central Coast | LONG JETTY |  | 280 | 3.358 | 176.25 | 1
D.F.ZN12610/000003 | D.F.ZN12610/000003 | 0 | Lower Central Coast | LONG JETTY |  |  |  | 0
D.F.ZN12610/000005 | D.F.ZN12610/000005 | 0 | Lower Central Coast | LONG JETTY |  | 295 | 1.7954 | 94.2326
D.F.ZN12610/000006 | D.F.ZN12610/000006 | 0 | Lower Central Coast | LONG JETTY |  | 370 | 2.6521 | 139.2012
D.F.ZN12610/000007 | D.F.ZN12610/000007 | 0 | Lower Central Coast | LONG JETTY |  | 325 | 1.6628 | 87.2739
D.F.ZN12610/000008 | D.F.ZN12610/000008 | 0 | Lower Central Coast | LONG JETTY |  |  |  | 0
D.F.ZN12610/000009 | D.F.ZN12610/000009 | 0 | Lower Central Coast | LONG JETTY |  | 290 | 2.1965 | 115.2879
D.F.ZN12610/000010 | D.F.ZN12610/000010 | 0 | Lower Central Coast | LONG JETTY |  | 320 | 4.5492 | 238.7704
D.F.ZN12610/000011 | D.F.ZN12610/000011 | 0 | Lower Central Coast | LONG JETTY |  | 400 | 3.1334 | 164.4585
D.F.ZN12610/000013 | D.F.ZN12610/000013 | 0 | Lower Central Coast | LONG JETTY |  | 295 | 2.699 | 141.6591
D.F.ZN12610/000014 | D.F.ZN12610/000014 | 0 | Lower Central Coast | LONG JETTY |  |  |  | 0
D.F.ZN12610/000016 | D.F.ZN12610/000016 | 0 | Lower Central Coast | LONG JETTY |  | 320 | 2.3288 | 122.2279
D.F.ZN12610/000017 | D.F.ZN12610/000017 | 0 | Lower Central Coast | LONG JETTY |  | 280 | 2.0248 | 106.2764
D.F.ZN12610/000018 | D.F.ZN12610/000018 | 0 | Lower Central Coast | LONG JETTY |  | 320 | 3.3417 | 175.3927
D.F.ZN12610/000020 | D.F.ZN12610/000020 | 0 | Lower Central Coast | LONG JETTY |  | 290 | 2.1022 | 110.335
D.F.ZN12610/000022 | D.F.ZN12610/000022 | 0 | Lower Central Coast | LONG JETTY |  | 370 | 2.4175 | 126.8865
D.F.ZN12610/000023 | D.F.ZN12610/000023 | 0 | Lower Central Coast | LONG JETTY |  | 295 | 2.6567 | 139.4427
D.F.ZN12610/000024 | D.F.ZN12610/000024 | 0 | Lower Central Coast | LONG JETTY |  | 290 | 2.2099 | 115.988
D.F.ZN12610/000025 | D.F.ZN12610/000025 | 0 | Lower Central Coast | LONG JETTY |  | 400 | 2.8438 | 149.2629
D.F.ZN12610/000026 | D.F.ZN12610/000026 | 0 | Lower Central Coast | LONG JETTY |  |  |  | 0
D.F.ZN12620/00001L | D.F.ZN12620/000001 | 0 | Upper Central Coast | NORAVILLE |  | 400 | 3.1212 | 163.8192
D.F.ZN12620/00001R | D.F.ZN12620/000001 | 1 | Upper Central Coast | NORAVILLE |  | 400 | 1.661 | 87.1796
D.F.ZN12620/000002 | D.F.ZN12620/000002 | 0 | Upper Central Coast | NORAVILLE |  | 265 | 0.9946 | 52.2018
D.F.ZN12620/000003 | D.F.ZN12620/000003 | 0 | Upper Central Coast | NORAVILLE |  | 315 | 2.1006 | 110.2546
D.F.ZN12620/000007 | D.F.ZN12620/000007 | 0 | Upper Central Coast | NORAVILLE |  | 305 | 3.4036 | 178.6447
D.F.ZN12620/000008 | D.F.ZN12620/000008 | 0 | Upper Central Coast | NORAVILLE |  | 305 | 2.6945 | 141.4257
D.F.ZN12620/000010 | D.F.ZN12620/000010 | 0 | Upper Central Coast | NORAVILLE |  | 295 | 2.4834 | 130.3468
D.F.ZN12620/000011 | D.F.ZN12620/000011 | 0 | Upper Central Coast | NORAVILLE |  | 330 | 3.7161 | 195.0442
D.F.ZN12620/000013 | D.F.ZN12620/000013 | 0 | Upper Central Coast | NORAVILLE |  | 325 | 2.142 | 112.4243
D.F.ZN12630/000001 | D.F.ZN12630/000001 | 0 | Lower Central Coast | PEATS RIDGE |  | 400 | 0.9742 | 51.1332
D.F.ZN12630/000002 | D.F.ZN12630/000002 | 0 | Lower Central Coast | PEATS RIDGE |  |  |  | 0
D.F.ZN12630/000003 | D.F.ZN12630/000003 | 0 | Lower Central Coast | PEATS RIDGE |  | 400 | 0.9677 | 50.7918
D.F.ZN12630/00006L | D.F.ZN12630/000006 | 0 | Lower Central Coast | PEATS RIDGE |  | 370 | 2.473 | 129.7973
D.F.ZN12630/00006R | D.F.ZN12630/000006 | 1 | Lower Central Coast | PEATS RIDGE |  |  |  | 0
D.F.ZN12630/000008 | D.F.ZN12630/000008 | 0 | Lower Central Coast | PEATS RIDGE |  | 370 | 3.0886 | 162.1074
D.F.ZN12630/000010 | D.F.ZN12630/000010 | 0 | Lower Central Coast | PEATS RIDGE |  | 400 | 2.6178 | 137.3987
D.F.ZN12630/000011 | D.F.ZN12630/000011 | 0 | Lower Central Coast | PEATS RIDGE |  | 400 | 0.8311 | 43.6195
D.F.ZN12630/000012 | D.F.ZN12630/000012 | 0 | Lower Central Coast | PEATS RIDGE |  |  |  | 0
D.F.ZN12630/00013L | D.F.ZN12630/000013 | 0 | Lower Central Coast | PEATS RIDGE |  | 400 | 1.6015 | 84.0588
D.F.ZN12630/00013R | D.F.ZN12630/000013 | 1 | Lower Central Coast | PEATS RIDGE |  |  |  | 0
D.F.ZN12640/000001 | D.F.ZN12640/000001 | 0 | Lower Central Coast | UMINA |  | 375 | 1.9877 | 104.3294
D.F.ZN12640/000002 | D.F.ZN12640/000002 | 0 | Lower Central Coast | UMINA |  | 375 | 2.4906 | 130.7227
D.F.ZN12640/000004 | D.F.ZN12640/000004 | 0 | Lower Central Coast | UMINA |  | 330 | 3.2758 | 171.9343
D.F.ZN12640/00005L | D.F.ZN12640/000005 | 0 | Lower Central Coast | UMINA |  | 305 | 2.8778 | 151.0459
D.F.ZN12640/00005R | D.F.ZN12640/000005 | 1 | Lower Central Coast | UMINA |  |  |  | 0
D.F.ZN12640/000007 | D.F.ZN12640/000007 | 0 | Lower Central Coast | UMINA |  | 370 | 2.8865 | 151.5024
D.F.ZN12640/000008 | D.F.ZN12640/000008 | 0 | Lower Central Coast | UMINA |  | 350 | 2.3017 | 120.81
D.F.ZN12640/000010 | D.F.ZN12640/000010 | 0 | Lower Central Coast | UMINA |  | 305 | 3.0907 | 162.2186
D.F.ZN12640/000012 | D.F.ZN12640/000012 | 0 | Lower Central Coast | UMINA |  | 355 | 3.0517 | 160.1712
D.F.ZN12640/00013L | D.F.ZN12640/000013 | 0 | Lower Central Coast | UMINA |  | 400 | 4.0697 | 213.6013
D.F.ZN12640/00013R | D.F.ZN12640/000013 | 1 | Lower Central Coast | UMINA |  |  |  | 0
D.F.ZN12640/000014 | D.F.ZN12640/000014 | 0 | Lower Central Coast | UMINA |  | 350 | 3.2543 | 170.8065
D.F.ZN12650/000001 | D.F.ZN12650/000001 | 0 | Lower Central Coast | WEST GOSFORD |  | 400 | 4.0043 | 210.1709
D.F.ZN12650/000002 | D.F.ZN12650/000002 | 0 | Lower Central Coast | WEST GOSFORD |  | 400 | 3.0183 | 158.4189
D.F.ZN12650/000003 | D.F.ZN12650/000003 | 0 | Lower Central Coast | WEST GOSFORD |  | 365 | 3.1232 | 163.9242 | 1
D.F.ZN12650/000005 | D.F.ZN12650/000005 | 0 | Lower Central Coast | WEST GOSFORD |  | 345 | 3.2715 | 171.71
D.F.ZN12650/000006 | D.F.ZN12650/000006 | 0 | Lower Central Coast | WEST GOSFORD |  | 380 | 4.3117 | 226.3038
D.F.ZN12650/000008 | D.F.ZN12650/000008 | 0 | Lower Central Coast | WEST GOSFORD |  | 345 | 0.8763 | 45.9935
D.F.ZN12650/00009L | D.F.ZN12650/000009 | 0 | Lower Central Coast | WEST GOSFORD |  | 290 | 3.8479 | 201.9639
D.F.ZN12650/00009R | D.F.ZN12650/000009 | 1 | Lower Central Coast | WEST GOSFORD |  | 367 | 1.8974 | 99.5852
D.F.ZN12650/000010 | D.F.ZN12650/000010 | 0 | Lower Central Coast | WEST GOSFORD |  | 320 | 2.6347 | 138.2843
D.F.ZN12650/00012L | D.F.ZN12650/000012 | 0 | Lower Central Coast | WEST GOSFORD |  | 320 | 3.4384 | 180.4684 | 1 | 305.3811
D.F.ZN12650/00012R | D.F.ZN12650/000012 | 1 | Lower Central Coast | WEST GOSFORD |  | 381 | 2.3799 | 124.9127 | 1
D.F.ZN12650/000013 | D.F.ZN12650/000013 | 0 | Lower Central Coast | WEST GOSFORD |  | 367 | 4.6957 | 246.4589
D.F.ZN12650/00014L | D.F.ZN12650/000014 | 0 | Lower Central Coast | WEST GOSFORD |  | 290 | 1.9077 | 100.1295
D.F.ZN12650/00014R | D.F.ZN12650/000014 | 1 | Lower Central Coast | WEST GOSFORD |  | 295 | 2.0814 | 109.2472
D.F.ZN12650/000016 | D.F.ZN12650/000016 | 0 | Lower Central Coast | WEST GOSFORD |  | 400 | 3.0309 | 159.0795
D.F.ZN12650/00017R | D.F.ZN12650/000017 | 0 | Lower Central Coast | WEST GOSFORD |  | 375 | 3.3515 | 175.9066
D.F.ZN12650/00017L | D.F.ZN12650/000017 | 1 | Lower Central Coast | WEST GOSFORD |  | 367 | 2.5665 | 134.7055
D.F.ZN12650/000019 | D.F.ZN12650/000019 | 0 | Lower Central Coast | WEST GOSFORD |  | 400 | 1.2103 | 63.5244
D.F.ZN12650/000020 | D.F.ZN12650/000020 | 0 | Lower Central Coast | WEST GOSFORD |  | 380 | 3.1622 | 165.9741
D.F.ZN12650/000021 | D.F.ZN12650/000021 | 0 | Lower Central Coast | WEST GOSFORD |  | 387 | 1.432 | 75.1605
D.F.ZN12660/000005 | D.F.ZN12660/000005 | 0 | Lower Central Coast | WOY WOY |  | 390 | 0.4924 | 25.8461
D.F.ZN12660/000006 | D.F.ZN12660/000006 | 0 | Lower Central Coast | WOY WOY |  | 290 | 1.1094 | 58.2273 | 1
D.F.ZN12660/000008 | D.F.ZN12660/000008 | 0 | Lower Central Coast | WOY WOY |  | 400 | 2.5062 | 131.544
D.F.ZN12660/00010L | D.F.ZN12660/000010 | 0 | Lower Central Coast | WOY WOY |  | 400 | 2.3043 | 120.9455
D.F.ZN12660/00010R | D.F.ZN12660/000010 | 1 | Lower Central Coast | WOY WOY |  | 400 | 1.518 | 79.6749
D.F.ZN12660/000011 | D.F.ZN12660/000011 | 0 | Lower Central Coast | WOY WOY |  | 400 | 2.0638 | 108.3239
D.F.ZN12660/000013 | D.F.ZN12660/000013 | 0 | Lower Central Coast | WOY WOY |  | 400 | 2.329 | 122.242
D.F.ZN12660/000014 | D.F.ZN12660/000014 | 0 | Lower Central Coast | WOY WOY |  | 400 | 2.8183 | 147.9211
D.F.ZN12660/000016 | D.F.ZN12660/000016 | 0 | Lower Central Coast | WOY WOY |  | 400 | 1.9738 | 103.5978
D.F.ZN12660/000017 | D.F.ZN12660/000017 | 0 | Lower Central Coast | WOY WOY |  | 400 | 2.5369 | 133.1529
D.F.ZN12690/000001 | D.F.ZN12690/000001 | 0 | Lower Central Coast | BERKELEY VALE |  | 305 | 3.1331 | 164.4428
D.F.ZN12690/000003 | D.F.ZN12690/000003 | 0 | Lower Central Coast | BERKELEY VALE |  | 350 | 2.0901 | 109.7032
D.F.ZN12690/000004 | D.F.ZN12690/000004 | 0 | Lower Central Coast | BERKELEY VALE |  | 400 | 2.4375 | 127.9356
D.F.ZN12690/000006 | D.F.ZN12690/000006 | 0 | Lower Central Coast | BERKELEY VALE |  | 400 | 2.4928 | 130.8387
D.F.ZN12690/000007 | D.F.ZN12690/000007 | 0 | Lower Central Coast | BERKELEY VALE |  | 375 | 3.9762 | 208.6978
D.F.ZN12690/000008 | D.F.ZN12690/000008 | 0 | Lower Central Coast | BERKELEY VALE |  | 305 | 2.0628 | 108.2691
D.F.ZN12690/000010 | D.F.ZN12690/000010 | 0 | Lower Central Coast | BERKELEY VALE |  | 355 | 1.4596 | 76.6098
D.F.ZN12690/000011 | D.F.ZN12690/000011 | 0 | Lower Central Coast | BERKELEY VALE |  | 280 | 3.334 | 174.9917
D.F.ZN12690/000012 | D.F.ZN12690/000012 | 0 | Lower Central Coast | BERKELEY VALE |  | 370 | 3.4874 | 183.0419
D.F.ZN12690/000014 | D.F.ZN12690/000014 | 0 | Lower Central Coast | BERKELEY VALE |  | 280 | 0.9651 | 50.6534
D.F.ZN12690/000016 | D.F.ZN12690/000016 | 0 | Lower Central Coast | BERKELEY VALE |  | 310 | 2.9563 | 155.1641
D.F.ZN12690/000017 | D.F.ZN12690/000017 | 0 | Lower Central Coast | BERKELEY VALE |  | 360 | 2.8959 | 151.9977
D.F.ZN12690/00019L | D.F.ZN12690/000019 | 0 | Lower Central Coast | BERKELEY VALE |  | 350 | 4.0803 | 214.1603
D.F.ZN12690/00019R | D.F.ZN12690/000019 | 1 | Lower Central Coast | BERKELEY VALE |  | 375 | 2.6486 | 139.013
D.F.ZN12690/000021 | D.F.ZN12690/000021 | 0 | Lower Central Coast | BERKELEY VALE |  | 375 | 2.1816 | 114.5067
D.F.ZN12690/00022L | D.F.ZN12690/000022 | 0 | Lower Central Coast | BERKELEY VALE |  | 350 |  | 0
D.F.ZN12690/00022R | D.F.ZN12690/000022 | 1 | Lower Central Coast | BERKELEY VALE |  | 375 |  | 0
D.F.ZN12690/00024L | D.F.ZN12690/000024 | 0 | Lower Central Coast | BERKELEY VALE |  | 310 | 1.49 | 78.2064
D.F.ZN12690/00024R | D.F.ZN12690/000024 | 1 | Lower Central Coast | BERKELEY VALE |  | 400 | 1.5145 | 79.4897
D.F.ZN12690/00026L | D.F.ZN12690/000026 | 0 | Lower Central Coast | BERKELEY VALE |  | 350 | 4.6174 | 242.3521
D.F.ZN12690/00026R | D.F.ZN12690/000026 | 1 | Lower Central Coast | BERKELEY VALE |  | 400 | 0.9918 | 52.0558
D.F.ZN13000/000001 | D.F.ZN13000/000001 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 1.5538 | 81.5512
D.F.ZN13000/00002R | D.F.ZN13000/000002 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 1.7151 | 90.0175
D.F.ZN13000/00002L | D.F.ZN13000/000002 | 1 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 1.4439 | 75.7839
D.F.ZN13000/000004 | D.F.ZN13000/000004 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 1.3854 | 72.7172
D.F.ZN13000/00005R | D.F.ZN13000/000005 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 320 | 3.8482 | 201.9777
D.F.ZN13000/00005L | D.F.ZN13000/000005 | 1 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 0.9249 | 48.5456
D.F.ZN13000/000007 | D.F.ZN13000/000007 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 390 | 7.2709 | 381.6226 | 1
D.F.ZN13000/00008L | D.F.ZN13000/000008 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 0.9528 | 50.0113
D.F.ZN13000/000010 | D.F.ZN13000/000010 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 370 | 2.0849 | 109.4283
D.F.ZN13000/00011L | D.F.ZN13000/000011 | 0 | Upper Central Coast | LAKE MUNMORAH |  | 400 | 4.7683 | 250.2687
D.F.ZN13000/00011R | D.F.ZN13000/000011 | 1 | Upper Central Coast | LAKE MUNMORAH |  |  |  | 0
D.F.ZN14143/000001 | D.F.ZN14143/000001 | 0 | Lower Central Coast | SOMERSBY |  |  |  | 0
D.F.ZN14143/000003 | D.F.ZN14143/000003 | 0 | Lower Central Coast | SOMERSBY |  |  |  | 0
D.F.ZN14143/000005 | D.F.ZN14143/000005 | 0 | Lower Central Coast | SOMERSBY |  | 355 | 4.1813 | 219.4606
D.F.ZN14143/000006 | D.F.ZN14143/000006 | 0 | Lower Central Coast | SOMERSBY |  | 350 | 3.4827 | 182.7923
D.F.ZN14143/000008 | D.F.ZN14143/000008 | 0 | Lower Central Coast | SOMERSBY |  | 290 | 1.1262 | 59.1122
D.F.ZN14143/000009 | D.F.ZN14143/000009 | 0 | Lower Central Coast | SOMERSBY |  |  |  | 0
D.F.ZN14143/000010 | D.F.ZN14143/000010 | 0 | Lower Central Coast | SOMERSBY |  | 385 | 0.3665 | 19.2338
D.F.ZN14143/000012 | D.F.ZN14143/000012 | 0 | Lower Central Coast | SOMERSBY |  | 367 | 2.0058 | 105.278
D.F.ZN14143/000014 | D.F.ZN14143/000014 | 0 | Lower Central Coast | SOMERSBY |  | 295 | 2.7525 | 144.471
D.F.ZN14143/000016 | D.F.ZN14143/000016 | 0 | Lower Central Coast | SOMERSBY |  | 295 | 4.1731 | 219.029 | 1
D.F.ZN14143/000017 | D.F.ZN14143/000017 | 0 | Lower Central Coast | SOMERSBY |  | 295 | 1.6122 | 84.6198 | 1
D.F.ZN14143/000019 | D.F.ZN14143/000019 | 0 | Lower Central Coast | SOMERSBY |  |  |  | 0
D.F.ZN14143/000020 | D.F.ZN14143/000020 | 0 | Lower Central Coast | SOMERSBY |  |  |  | 0
D.F.ZN14143/000021 | D.F.ZN14143/000021 | 0 | Lower Central Coast | SOMERSBY |  | 400 | 1.5023 | 78.8492
D.F.ZN14144/00001L | D.F.ZN14144/000001 | 0 | Lower Central Coast | WAMBERAL |  | 320 | 2.9887 | 156.8656
D.F.ZN14144/00001R | D.F.ZN14144/000001 | 1 | Lower Central Coast | WAMBERAL |  |  |  | 0
D.F.ZN14144/000002 | D.F.ZN14144/000002 | 0 | Lower Central Coast | WAMBERAL |  | 320 | 2.6081 | 136.8879
D.F.ZN14144/00004L | D.F.ZN14144/000004 | 0 | Lower Central Coast | WAMBERAL |  | 400 | 1.6779 | 88.0666
D.F.ZN14144/00004R | D.F.ZN14144/000004 | 1 | Lower Central Coast | WAMBERAL |  |  |  | 0
D.F.ZN14144/000005 | D.F.ZN14144/000005 | 0 | Lower Central Coast | WAMBERAL |  | 385 | 0.8851 | 46.4536
D.F.ZN14144/00007L | D.F.ZN14144/000007 | 0 | Lower Central Coast | WAMBERAL |  | 365 | 2.2943 | 120.42
D.F.ZN14144/00007R | D.F.ZN14144/000007 | 1 | Lower Central Coast | WAMBERAL |  |  |  | 0
D.F.ZN14144/000008 | D.F.ZN14144/000008 | 0 | Lower Central Coast | WAMBERAL |  | 385 | 1.0774 | 56.549
D.F.ZN14144/00010L | D.F.ZN14144/000010 | 0 | Lower Central Coast | WAMBERAL |  | 400 | 2.8325 | 148.6699
D.F.ZN14144/00010R | D.F.ZN14144/000010 | 1 | Lower Central Coast | WAMBERAL |  |  |  | 0
D.F.ZN14144/000011 | D.F.ZN14144/000011 | 0 | Lower Central Coast | WAMBERAL |  |  |  | 0
D.F.ZN14460/000661 | D.F.ZN14460/000661 | 0 | Upper Central Coast | VALES POINT |  | 400 | 4.6546 | 244.3043
D.F.ZN14460/000662 | D.F.ZN14460/000662 | 0 | Upper Central Coast | VALES POINT |  | 400 | 4.3934 | 230.5943
D.F.ZN14460/000663 | D.F.ZN14460/000663 | 0 | Upper Central Coast | VALES POINT |  | 337 |  | 0
D.F.ZN14460/000664 | D.F.ZN14460/000664 | 0 | Upper Central Coast | VALES POINT |  | 400 | 3.2913 | 172.7482
D.F.ZN14891/00001L | D.F.ZN14891/000001 | 0 | Upper Central Coast | WYONG |  | 285 |  | 0
D.F.ZN14891/00001R | D.F.ZN14891/000001 | 1 | Upper Central Coast | WYONG |  |  |  | 0
D.F.ZN14891/00003L | D.F.ZN14891/000003 | 0 | Upper Central Coast | WYONG |  | 285 |  | 0 | 1
D.F.ZN14891/00003R | D.F.ZN14891/000003 | 1 | Upper Central Coast | WYONG |  |  |  | 0 | 1
D.F.ZN14891/000005 | D.F.ZN14891/000005 | 0 | Upper Central Coast | WYONG |  | 285 | 4.1875 | 219.7851 | 1
D.F.ZN14891/00006L | D.F.ZN14891/000006 | 0 | Upper Central Coast | WYONG |  | 315 |  | 0
D.F.ZN14891/00006R | D.F.ZN14891/000006 | 1 | Upper Central Coast | WYONG |  |  |  | 0
D.F.ZN14891/000008 | D.F.ZN14891/000008 | 0 | Upper Central Coast | WYONG |  | 350 | 3.4495 | 181.0528
D.F.ZN14891/00009L | D.F.ZN14891/000009 | 0 | Upper Central Coast | WYONG |  | 305 |  | 0
D.F.ZN14891/00009R | D.F.ZN14891/000009 | 1 | Upper Central Coast | WYONG |  |  |  | 0
D.F.ZN14891/000010 | D.F.ZN14891/000010 | 0 | Upper Central Coast | WYONG |  | 355 | 4.5355 | 238.0526 | 1
D.F.ZN14891/00012L | D.F.ZN14891/000012 | 0 | Upper Central Coast | WYONG |  | 370 |  | 0 | 1
D.F.ZN14891/00012R | D.F.ZN14891/000012 | 1 | Upper Central Coast | WYONG |  |  |  | 0 | 1
D.F.ZN14891/00014R | D.F.ZN14891/000014 | 0 | Upper Central Coast | WYONG |  | 370 | 3.25 | 170.5816 | 1 | 183.2664
D.F.ZN14891/00014L | D.F.ZN14891/000014 | 1 | Upper Central Coast | WYONG |  | 280 | 0.2417 | 12.6848 | 1
D.F.ZN14891/000016 | D.F.ZN14891/000016 | 0 | Upper Central Coast | WYONG |  | 305 | 4.2196 | 221.4695
D.F.ZN14891/00017L | D.F.ZN14891/000017 | 0 | Upper Central Coast | WYONG |  | 300 |  | 0
D.F.ZN14891/00017R | D.F.ZN14891/000017 | 1 | Upper Central Coast | WYONG |  |  |  | 0
D.F.ZN14891/000019 | D.F.ZN14891/000019 | 0 | Upper Central Coast | WYONG |  | 280 | 1.2349 | 64.8171
D.F.ZN14891/00020L | D.F.ZN14891/000020 | 0 | Upper Central Coast | WYONG | 1 | 300 |  | 0
D.F.ZN14891/00020R | D.F.ZN14891/000020 | 1 | Upper Central Coast | WYONG |  |  |  | 0
D.F.ZN14891/000021 | D.F.ZN14891/000021 | 0 | Upper Central Coast | WYONG |  | 400 | 2.8559 | 149.8958
D.F.ZN14892/00001L | D.F.ZN14892/000001 | 0 | Upper Central Coast | CHARMHAVEN |  | 355 |  | 0 | 1
D.F.ZN14892/00001R | D.F.ZN14892/000001 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0 | 1
D.F.ZN14892/00002R | D.F.ZN14892/000002 | 0 | Upper Central Coast | CHARMHAVEN |  |  |  | 0
D.F.ZN14892/00003L | D.F.ZN14892/000003 | 0 | Upper Central Coast | CHARMHAVEN |  | 305 |  | 0
D.F.ZN14892/00003R | D.F.ZN14892/000003 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0
D.F.ZN14892/000005 | D.F.ZN14892/000005 | 0 | Upper Central Coast | CHARMHAVEN |  | 365 | 2.6378 | 138.4475
D.F.ZN14892/00006L | D.F.ZN14892/000006 | 0 | Upper Central Coast | CHARMHAVEN |  | 305 |  | 0
D.F.ZN14892/00006R | D.F.ZN14892/000006 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0
D.F.ZN14892/000008 | D.F.ZN14892/000008 | 0 | Upper Central Coast | CHARMHAVEN |  | 400 | 2.3027 | 120.8625
D.F.ZN14892/00009L | D.F.ZN14892/000009 | 0 | Upper Central Coast | CHARMHAVEN |  | 305 |  | 0 | 1
D.F.ZN14892/00009R | D.F.ZN14892/000009 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0 | 1
D.F.ZN14892/000010 | D.F.ZN14892/000010 | 0 | Upper Central Coast | CHARMHAVEN |  | 315 | 3.5508 | 186.3701 | 1
D.F.ZN14892/00012L | D.F.ZN14892/000012 | 0 | Upper Central Coast | CHARMHAVEN |  | 370 |  | 0 | 1
D.F.ZN14892/00012R | D.F.ZN14892/000012 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0 | 1
D.F.ZN14892/00013L | D.F.ZN14892/000013 | 0 | Upper Central Coast | CHARMHAVEN |  | 375 |  | 0
D.F.ZN14892/00014L | D.F.ZN14892/000014 | 0 | Upper Central Coast | CHARMHAVEN |  | 305 |  | 0
D.F.ZN14892/00014R | D.F.ZN14892/000014 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0
D.F.ZN14892/000016 | D.F.ZN14892/000016 | 0 | Upper Central Coast | CHARMHAVEN |  | 330 | 4.5522 | 238.9267
D.F.ZN14892/00017L | D.F.ZN14892/000017 | 0 | Upper Central Coast | CHARMHAVEN |  | 365 |  | 0
D.F.ZN14892/00017R | D.F.ZN14892/000017 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0
D.F.ZN14892/000019 | D.F.ZN14892/000019 | 0 | Upper Central Coast | CHARMHAVEN |  | 305 | 3.9357 | 206.5728
D.F.ZN14892/00020L | D.F.ZN14892/000020 | 0 | Upper Central Coast | CHARMHAVEN |  | 310 |  | 0
D.F.ZN14892/00020R | D.F.ZN14892/000020 | 1 | Upper Central Coast | CHARMHAVEN |  |  |  | 0
D.F.ZN14892/000021 | D.F.ZN14892/000021 | 0 | Upper Central Coast | CHARMHAVEN |  | 330 | 3.2137 | 168.6734
D.F.ZN15001/00002L | D.F.ZN15001/000002 | 0 | Manly Warringah | BROOKVALE |  | 400 | 3.9839 | 209.1013
D.F.ZN15001/00002R | D.F.ZN15001/000002 | 1 | Manly Warringah | BROOKVALE |  | 400 | 2.1361 | 112.1173
D.F.ZN15001/000003 | D.F.ZN15001/000003 | 0 | Manly Warringah | BROOKVALE |  | 400 | 2.9322 | 153.9015
D.F.ZN15001/00004L | D.F.ZN15001/000004 | 0 | Manly Warringah | BROOKVALE |  | 400 | 3.222 | 169.1132
D.F.ZN15001/00006L | D.F.ZN15001/000006 | 0 | Manly Warringah | BROOKVALE |  | 400 | 3.1472 | 165.1844
D.F.ZN15001/000008 | D.F.ZN15001/000008 | 0 | Manly Warringah | BROOKVALE |  | 400 | 2.5015 | 131.2952
D.F.ZN15001/00010L | D.F.ZN15001/000010 | 0 | Manly Warringah | BROOKVALE |  | 400 | 5.2355 | 274.7936
D.F.ZN15001/00010R | D.F.ZN15001/000010 | 1 | Manly Warringah | BROOKVALE |  | 400 | 0.2849 | 14.9509
D.F.ZN15001/00011L | D.F.ZN15001/000011 | 0 | Manly Warringah | BROOKVALE |  | 400 | 2.2108 | 116.0375
D.F.ZN15001/00011R | D.F.ZN15001/000011 | 1 | Manly Warringah | BROOKVALE |  | 400 | 1.5222 | 79.8922
D.F.ZN15001/000013 | D.F.ZN15001/000013 | 0 | Manly Warringah | BROOKVALE |  | 295 |  | 0
D.F.ZN15001/000015 | D.F.ZN15001/000015 | 0 | Manly Warringah | BROOKVALE |  | 355 | 4.0605 | 213.1201
D.F.ZN15001/000016 | D.F.ZN15001/000016 | 0 | Manly Warringah | BROOKVALE |  | 310 | 3.1056 | 163.0027
D.F.ZN15001/000017 | D.F.ZN15001/000017 | 0 | Manly Warringah | BROOKVALE |  | 350 | 0.5642 | 29.6121
D.F.ZN15001/00018L | D.F.ZN15001/000018 | 0 | Manly Warringah | BROOKVALE |  | 395 | 4.6268 | 242.8434
D.F.ZN15001/00018R | D.F.ZN15001/000018 | 1 | Manly Warringah | BROOKVALE |  | 310 | 1.2063 | 63.3153
D.F.ZN15002/000002 | D.F.ZN15002/000002 | 0 | Pittwater & Northern Beaches | NARRABEEN |  | 370 | 2.9202 | 153.2694
D.F.ZN15002/000004 | D.F.ZN15002/000004 | 0 | Pittwater & Northern Beaches | NARRABEEN |  | 295 | 1.5209 | 79.8266
D.F.ZN15002/000006 | D.F.ZN15002/000006 | 0 | Pittwater & Northern Beaches | NARRABEEN |  | 380 | 4.0973 | 215.0521
D.F.ZN15002/000008 | D.F.ZN15002/000008 | 0 | Pittwater & Northern Beaches | NARRABEEN |  | 370 | 3.371 | 176.9328
D.F.ZN15002/000009 | D.F.ZN15002/000009 | 0 | Pittwater & Northern Beaches | NARRABEEN |  | 330 | 0.0352 | 1.8495
D.F.ZN15004/000001 | D.F.ZN15004/000001 | 0 | Pittwater & Northern Beaches | NEWPORT |  | 400 | 3.2428 | 170.2007
D.F.ZN15004/000003 | D.F.ZN15004/000003 | 0 | Pittwater & Northern Beaches | NEWPORT |  | 325 | 2.9605 | 155.3878
D.F.ZN15004/000005 | D.F.ZN15004/000005 | 0 | Pittwater & Northern Beaches | NEWPORT |  | 385 | 4.0543 | 212.7947
D.F.ZN15004/000009 | D.F.ZN15004/000009 | 0 | Pittwater & Northern Beaches | NEWPORT |  | 400 | 2.7796 | 145.8898
D.F.ZN15005/00002L | D.F.ZN15005/000002 | 0 | Manly Warringah | BELROSE |  | 400 | 2.4864 | 130.4997
D.F.ZN15005/00002R | D.F.ZN15005/000002 | 1 | Manly Warringah | BELROSE |  | 400 | 2.5767 | 135.2403
D.F.ZN15005/000004 | D.F.ZN15005/000004 | 0 | Manly Warringah | BELROSE |  | 400 | 3.068 | 161.028
D.F.ZN15005/000006 | D.F.ZN15005/000006 | 0 | Manly Warringah | BELROSE |  | 400 | 3.4408 | 180.5955
D.F.ZN15005/00008R | D.F.ZN15005/000008 | 0 | Manly Warringah | BELROSE |  | 400 | 2.5718 | 134.9863
D.F.ZN15005/00008L | D.F.ZN15005/000008 | 1 | Manly Warringah | BELROSE |  | 370 | 2.1676 | 113.7669
D.F.ZN15005/000010 | D.F.ZN15005/000010 | 0 | Manly Warringah | BELROSE |  | 370 | 3.985 | 209.1564
D.F.ZN15005/00012L | D.F.ZN15005/000012 | 0 | Manly Warringah | BELROSE |  | 400 | 3.3769 | 177.239
D.F.ZN15005/00012R | D.F.ZN15005/000012 | 1 | Manly Warringah | BELROSE |  | 370 | 0.2419 | 12.6953
D.F.ZN15006/00001L | D.F.ZN15006/000001 | 0 | Manly Warringah | DEE WHY WEST |  | 325 | 1.2288 | 64.4939
D.F.ZN15006/00002L | D.F.ZN15006/000002 | 0 | Manly Warringah | DEE WHY WEST |  | 340 | 3.4653 | 181.8785
D.F.ZN15006/000004 | D.F.ZN15006/000004 | 0 | Manly Warringah | DEE WHY WEST |  | 390 | 1.9742 | 103.6195
D.F.ZN15006/00006L | D.F.ZN15006/000006 | 0 | Manly Warringah | DEE WHY WEST |  | 400 | 1.8917 | 99.2904
D.F.ZN15006/00006R | D.F.ZN15006/000006 | 1 | Manly Warringah | DEE WHY WEST |  | 400 | 0.1236 | 6.4873
D.F.ZN15006/000008 | D.F.ZN15006/000008 | 0 | Manly Warringah | DEE WHY WEST |  | 400 | 3.3915 | 178.0077
D.F.ZN15006/000009 | D.F.ZN15006/000009 | 0 | Manly Warringah | DEE WHY WEST |  | 400 | 4.3051 | 225.9576
D.F.ZN15006/00012L | D.F.ZN15006/000012 | 0 | Manly Warringah | DEE WHY WEST |  | 330 | 3.5714 | 187.4483
D.F.ZN15006/00012R | D.F.ZN15006/000012 | 1 | Manly Warringah | DEE WHY WEST |  | 370 | 3.3904 | 177.9523
D.F.ZN15006/000013 | D.F.ZN15006/000013 | 0 | Manly Warringah | DEE WHY WEST |  | 400 | 3.254 | 170.7902
D.F.ZN15006/000014 | D.F.ZN15006/000014 | 0 | Manly Warringah | DEE WHY WEST |  | 350 | 1.9913 | 104.5184
D.F.ZN15006/000015 | D.F.ZN15006/000015 | 0 | Manly Warringah | DEE WHY WEST |  | 370 | 3.3644 | 176.5831
D.F.ZN15006/00016R | D.F.ZN15006/000016 | 0 | Manly Warringah | DEE WHY WEST |  | 390 | 3.0987 | 162.6416
D.F.ZN15006/00016L | D.F.ZN15006/000016 | 1 | Manly Warringah | DEE WHY WEST |  | 325 | 2.2825 | 119.7983
D.F.ZN15008/000001 | D.F.ZN15008/000001 | 0 | Manly Warringah | HARBORD |  | 330 | 2.8398 | 149.0514
D.F.ZN15008/000003 | D.F.ZN15008/000003 | 0 | Manly Warringah | HARBORD |  | 350 | 0.8291 | 43.5188
D.F.ZN15008/000004 | D.F.ZN15008/000004 | 0 | Manly Warringah | HARBORD |  | 350 | 0.7607 | 39.9287
D.F.ZN15008/000005 | D.F.ZN15008/000005 | 0 | Manly Warringah | HARBORD |  | 370 | 3.046 | 159.8754
D.F.ZN15008/000006 | D.F.ZN15008/000006 | 0 | Manly Warringah | HARBORD |  | 370 | 1.6981 | 89.1294
D.F.ZN15008/000007 | D.F.ZN15008/000007 | 0 | Manly Warringah | HARBORD |  | 400 | 4.6996 | 246.6664
D.F.ZN15008/00009L | D.F.ZN15008/000009 | 0 | Manly Warringah | HARBORD |  | 400 | 4.6149 | 242.2214
D.F.ZN15008/000010 | D.F.ZN15008/000010 | 0 | Manly Warringah | HARBORD |  | 400 | 3.5747 | 187.6247
D.F.ZN15009/00001L | D.F.ZN15009/000001 | 0 | Manly Warringah | MANLY |  | 295 | 2.9086 | 152.6595
D.F.ZN15009/00001R | D.F.ZN15009/000001 | 1 | Manly Warringah | MANLY |  | 330 | 1.8091 | 94.952
D.F.ZN15009/000003 | D.F.ZN15009/000003 | 0 | Manly Warringah | MANLY |  | 400 | 1.3732 | 72.0764
D.F.ZN15009/000005 | D.F.ZN15009/000005 | 0 | Manly Warringah | MANLY |  | 400 | 2.9662 | 155.6841
D.F.ZN15009/000007 | D.F.ZN15009/000007 | 0 | Manly Warringah | MANLY |  | 360 | 3.0137 | 158.1774
D.F.ZN15009/000009 | D.F.ZN15009/000009 | 0 | Manly Warringah | MANLY |  | 345 | 1.7811 | 93.4858
D.F.ZN15009/000011 | D.F.ZN15009/000011 | 0 | Manly Warringah | MANLY |  | 400 | 4.0163 | 210.7993
D.F.ZN15009/000012 | D.F.ZN15009/000012 | 0 | Manly Warringah | MANLY |  | 370 | 2.0853 | 109.4475
D.F.ZN15010/000024 | D.F.ZN15010/000024 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 325 | 3.3241 | 174.47
D.F.ZN15010/000025 | D.F.ZN15010/000025 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 370 | 1.0408 | 54.63
D.F.ZN15010/000026 | D.F.ZN15010/000026 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 295 | 0.7328 | 38.4601
D.F.ZN15010/000028 | D.F.ZN15010/000028 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 370 | 2.5059 | 131.5278
D.F.ZN15010/000029 | D.F.ZN15010/000029 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 325 | 1.1633 | 61.057
D.F.ZN15010/000030 | D.F.ZN15010/000030 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 325 | 3.9431 | 206.9613
D.F.ZN15010/000033 | D.F.ZN15010/000033 | 0 | Pittwater & Northern Beaches | CAREEL BAY |  | 330 | 0.2175 | 11.4183
D.F.ZN15011/00001L | D.F.ZN15011/000001 | 0 | Manly Warringah | BEACON HILL |  | 400 | 2.4448 | 128.3205
D.F.ZN15011/00002L | D.F.ZN15011/000002 | 0 | Manly Warringah | BEACON HILL |  | 375 | 3.5884 | 188.3442
D.F.ZN15011/00002R | D.F.ZN15011/000002 | 1 | Manly Warringah | BEACON HILL |  | 295 | 1.9685 | 103.318
D.F.ZN15011/000004 | D.F.ZN15011/000004 | 0 | Manly Warringah | BEACON HILL |  | 400 | 2.7682 | 145.2918
D.F.ZN15011/00006R | D.F.ZN15011/000006 | 0 | Manly Warringah | BEACON HILL |  | 400 | 3.1668 | 166.2164
D.F.ZN15011/00008L | D.F.ZN15011/000008 | 0 | Manly Warringah | BEACON HILL |  | 295 | 2.7145 | 142.4767
D.F.ZN15011/00010R | D.F.ZN15011/000010 | 0 | Manly Warringah | BEACON HILL |  | 365 | 3.3101 | 173.7375
D.F.ZN15011/00010L | D.F.ZN15011/000010 | 1 | Manly Warringah | BEACON HILL |  | 295 | 1.7589 | 92.3174
D.F.ZN15012/000002 | D.F.ZN15012/000002 | 0 | Manly Warringah | KILLARNEY |  | 400 | 3.4362 | 180.3543
D.F.ZN15012/000004 | D.F.ZN15012/000004 | 0 | Manly Warringah | KILLARNEY |  | 320 | 2.8722 | 150.7537
D.F.ZN15012/00006L | D.F.ZN15012/000006 | 0 | Manly Warringah | KILLARNEY |  | 400 | 3.4206 | 179.5359
D.F.ZN15012/000008 | D.F.ZN15012/000008 | 0 | Manly Warringah | KILLARNEY |  | 400 | 2.8188 | 147.9481
D.F.ZN15013/000001 | D.F.ZN15013/000001 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 400 | 4.5527 | 238.9525
D.F.ZN15013/000002 | D.F.ZN15013/000002 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 400 | 0.9043 | 47.4645
D.F.ZN15013/000004 | D.F.ZN15013/000004 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 320 | 3.9145 | 205.4576
D.F.ZN15013/000006 | D.F.ZN15013/000006 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 400 | 0.9748 | 51.1631
D.F.ZN15013/000008 | D.F.ZN15013/000008 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 400 | 2.3404 | 122.8393
D.F.ZN15013/000010 | D.F.ZN15013/000010 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 400 | 1.7612 | 92.4387
D.F.ZN15013/000012 | D.F.ZN15013/000012 | 0 | Pittwater & Northern Beaches | TERREY HILLS |  | 365 | 2.1318 | 111.8879
D.F.ZN15014/000005 | D.F.ZN15014/000005 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 400 | 4.5547 | 239.0609
D.F.ZN15014/000007 | D.F.ZN15014/000007 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 350 | 2.7692 | 145.3432
D.F.ZN15014/00008L | D.F.ZN15014/000008 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 400 | 2.8048 | 147.2147
D.F.ZN15014/000010 | D.F.ZN15014/000010 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 395 | 3.4479 | 180.9691
D.F.ZN15014/00011L | D.F.ZN15014/000011 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 310 | 1.6406 | 86.1096
D.F.ZN15014/000014 | D.F.ZN15014/000014 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 350 | 4.5657 | 239.6371
D.F.ZN15014/000016 | D.F.ZN15014/000016 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 310 | 1.7706 | 92.9322
D.F.ZN15014/000018 | D.F.ZN15014/000018 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 355 | 1.3634 | 71.5619
D.F.ZN15014/00019L | D.F.ZN15014/000019 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 400 | 3.6348 | 190.7762
D.F.ZN15014/000020 | D.F.ZN15014/000020 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 310 | 2.9979 | 157.3474
D.F.ZN15014/000022 | D.F.ZN15014/000022 | 0 | Pittwater & Northern Beaches | MONA VALE |  | 315 | 3.3912 | 177.9897
D.F.ZN15015/000004 | D.F.ZN15015/000004 | 0 | Manly Warringah | NORTH HEAD |  | 800 | 8.3712 | 439.3741
D.F.ZN15015/000005 | D.F.ZN15015/000005 | 0 | Manly Warringah | NORTH HEAD |  | 400 | 2.5464 | 133.6525
D.F.ZN15015/000009 | D.F.ZN15015/000009 | 0 | Manly Warringah | NORTH HEAD |  | 400 | 5.5488 | 291.2365
D.F.ZN15015/000011 | D.F.ZN15015/000011 | 0 | Manly Warringah | NORTH HEAD |  | 400 | 5.5008 | 288.7171
D.F.ZN15015/000015 | D.F.ZN15015/000015 | 0 | Manly Warringah | NORTH HEAD |  | 400 | 1.7478 | 91.7342
D.F.ZN35335/00004L | D.F.ZN35335/000004 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 1.1157 | 58.557
D.F.ZN35335/00004R | D.F.ZN35335/000004 | 1 | Lower North Shore | RNS HOSPITAL |  | 315 |  | 0
D.F.ZN35335/000006 | D.F.ZN35335/000006 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 0.8506 | 44.6474
D.F.ZN35335/00008L | D.F.ZN35335/000008 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 0.8883 | 46.6216
D.F.ZN35335/000009 | D.F.ZN35335/000009 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 2.4409 | 128.115
D.F.ZN35335/000012 | D.F.ZN35335/000012 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 2.2476 | 117.9706
D.F.ZN35335/00014R | D.F.ZN35335/000014 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 2.5208 | 132.3076
D.F.ZN35335/00016R | D.F.ZN35335/000016 | 0 | Lower North Shore | RNS HOSPITAL |  | 310 | 0.9509 | 49.9101
D.F.ZN35335/000017 | D.F.ZN35335/000017 | 0 | Lower North Shore | RNS HOSPITAL |  | 400 | 1.1167 | 58.6092
D.F.ZN35370/000002 | D.F.ZN35370/000002 | 0 | North West Sydney | GALSTON |  | 400 | 1.8001 | 94.4826
D.F.ZN35370/00004L | D.F.ZN35370/000004 | 0 | North West Sydney | GALSTON |  | 400 | 2.7554 | 144.6189
D.F.ZN35370/000008 | D.F.ZN35370/000008 | 0 | North West Sydney | GALSTON |  | 400 | 2.6149 | 137.246
D.F.ZN35370/00010L | D.F.ZN35370/000010 | 0 | North West Sydney | GALSTON |  | 400 | 3.0911 | 162.2409
D.F.ZN35400/000051 | D.F.ZN35400/000051 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 0.3039 | 15.9485
D.F.ZN35400/000052 | D.F.ZN35400/000052 | 0 | Lower North Shore | NORTH SYDNEY |  | 385 | 3.0443 | 159.7853
D.F.ZN35400/000053 | D.F.ZN35400/000053 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 0.8889 | 46.6548
D.F.ZN35400/000056 | D.F.ZN35400/000056 | 0 | Lower North Shore | NORTH SYDNEY |  | 325 | 2.0853 | 109.4479
D.F.ZN35400/000059 | D.F.ZN35400/000059 | 0 | Lower North Shore | NORTH SYDNEY |  | 285 | 0.6027 | 31.6318
D.F.ZN35400/000060 | D.F.ZN35400/000060 | 0 | Lower North Shore | NORTH SYDNEY |  | 280 | 1.8448 | 96.8254
D.F.ZN35400/000061 | D.F.ZN35400/000061 | 0 | Lower North Shore | NORTH SYDNEY |  | 245 | 2.0254 | 106.3078
D.F.ZN35400/000062 | D.F.ZN35400/000062 | 0 | Lower North Shore | NORTH SYDNEY |  | 275 | 1.9525 | 102.4805
D.F.ZN35400/000064 | D.F.ZN35400/000064 | 0 | Lower North Shore | NORTH SYDNEY |  | 300 | 1.6663 | 87.4565
D.F.ZN35400/000067 | D.F.ZN35400/000067 | 0 | Lower North Shore | NORTH SYDNEY |  | 245 | 1.8666 | 97.973
D.F.ZN35400/000068 | D.F.ZN35400/000068 | 0 | Lower North Shore | NORTH SYDNEY |  | 385 | 2.3009 | 120.7668
D.F.ZN35400/000071 | D.F.ZN35400/000071 | 0 | Lower North Shore | NORTH SYDNEY |  | 275 | 1.3649 | 71.6364
D.F.ZN35400/000072 | D.F.ZN35400/000072 | 0 | Lower North Shore | NORTH SYDNEY |  | 285 | 0.9053 | 47.515
D.F.ZN35400/000073 | D.F.ZN35400/000073 | 0 | Lower North Shore | NORTH SYDNEY |  | 245 | 2.3188 | 121.7078
D.F.ZN35400/000076 | D.F.ZN35400/000076 | 0 | Lower North Shore | NORTH SYDNEY |  | 390 | 0.7685 | 40.3342
D.F.ZN35400/000077 | D.F.ZN35400/000077 | 0 | Lower North Shore | NORTH SYDNEY |  | 245 | 1.9673 | 103.2539
D.F.ZN35400/000079 | D.F.ZN35400/000079 | 0 | Lower North Shore | NORTH SYDNEY |  | 355 | 2.9412 | 154.3725
D.F.ZN35400/000080 | D.F.ZN35400/000080 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 1.8503 | 97.1147
D.F.ZN35400/000081 | D.F.ZN35400/000081 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 3.4219 | 179.6044
D.F.ZN35400/000082 | D.F.ZN35400/000082 | 0 | Lower North Shore | NORTH SYDNEY |  | 325 | 4.6292 | 242.9709
D.F.ZN35400/000083 | D.F.ZN35400/000083 | 0 | Lower North Shore | NORTH SYDNEY |  | 285 | 1.8503 | 97.1178
D.F.ZN35400/000085 | D.F.ZN35400/000085 | 0 | Lower North Shore | NORTH SYDNEY |  | 265 | 1.7365 | 91.141
D.F.ZN35400/000086 | D.F.ZN35400/000086 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 1.8657 | 97.9218
D.F.ZN35400/000088 | D.F.ZN35400/000088 | 0 | Lower North Shore | NORTH SYDNEY |  | 300 | 2.441 | 128.1178
D.F.ZN35400/000089 | D.F.ZN35400/000089 | 0 | Lower North Shore | NORTH SYDNEY |  | 265 | 1.8155 | 95.2868
D.F.ZN35400/000090 | D.F.ZN35400/000090 | 0 | Lower North Shore | NORTH SYDNEY |  | 265 | 0.2199 | 11.5399
D.F.ZN35400/000093 | D.F.ZN35400/000093 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 0.5887 | 30.8997
D.F.ZN35400/000094 | D.F.ZN35400/000094 | 0 | Lower North Shore | NORTH SYDNEY |  | 400 | 1.3269 | 69.6425
D.F.ZN35400/000095 | D.F.ZN35400/000095 | 0 | Lower North Shore | NORTH SYDNEY |  | 370 | 2.3758 | 124.6996
D.F.ZN35400/000097 | D.F.ZN35400/000097 | 0 | Lower North Shore | NORTH SYDNEY |  | 300 | 1.8633 | 97.7996
D.F.ZN35400/000101 | D.F.ZN35400/000101 | 0 | Lower North Shore | NORTH SYDNEY |  | 265 | 1.6151 | 84.7724
D.F.ZN35400/000102 | D.F.ZN35400/000102 | 0 | Lower North Shore | NORTH SYDNEY |  | 290 | 2.0617 | 108.2106
D.F.ZN35400/000103 | D.F.ZN35400/000103 | 0 | Lower North Shore | NORTH SYDNEY |  | 265 | 2.0131 | 105.6585
D.F.ZN35400/000106 | D.F.ZN35400/000106 | 0 | Lower North Shore | NORTH SYDNEY |  | 345 | 2.3646 | 124.1103
D.F.ZN35400/000109 | D.F.ZN35400/000109 | 0 | Lower North Shore | NORTH SYDNEY |  | 305 | 3.0299 | 159.0308
D.F.ZN35400/000110 | D.F.ZN35400/000110 | 0 | Lower North Shore | NORTH SYDNEY |  | 290 | 2.9775 | 156.2788
D.F.ZN35500/00014L | D.F.ZN35500/000014 | 0 | Carlingford | TOP RYDE |  | 370 | 3.0077 | 157.8623
D.F.ZN35500/000015 | D.F.ZN35500/000015 | 0 | Carlingford | TOP RYDE |  | 400 | 0.7378 | 38.7252
D.F.ZN35500/00016L | D.F.ZN35500/000016 | 0 | Carlingford | TOP RYDE |  | 315 | 3.3823 | 177.5255
D.F.ZN35500/000018 | D.F.ZN35500/000018 | 0 | Carlingford | TOP RYDE |  | 295 | 2.9421 | 154.4196
D.F.ZN35500/00019L | D.F.ZN35500/000019 | 0 | Carlingford | TOP RYDE |  | 310 | 2.7945 | 146.6756
D.F.ZN35500/000020 | D.F.ZN35500/000020 | 0 | Carlingford | TOP RYDE |  | 375 | 3.0867 | 162.0109
D.F.ZN35500/00022L | D.F.ZN35500/000022 | 0 | Carlingford | TOP RYDE |  | 305 | 2.5842 | 135.6368
D.F.ZN35500/000023 | D.F.ZN35500/000023 | 0 | Carlingford | TOP RYDE |  | 295 | 2.6176 | 137.3892
D.F.ZN35500/00024L | D.F.ZN35500/000024 | 0 | Carlingford | TOP RYDE |  | 400 | 1.1724 | 61.5358
D.F.ZN35500/00024R | D.F.ZN35500/000024 | 1 | Carlingford | TOP RYDE |  | 400 | 0.9098 | 47.7496
D.F.ZN35500/00026L | D.F.ZN35500/000026 | 0 | Carlingford | TOP RYDE |  | 400 | 3.3284 | 174.6977
D.F.ZN35500/000027 | D.F.ZN35500/000027 | 0 | Carlingford | TOP RYDE |  | 330 | 2.9236 | 153.4502
D.F.ZN35500/00028L | D.F.ZN35500/000028 | 0 | Carlingford | TOP RYDE |  | 290 | 4.1764 | 219.2053
D.F.ZN35500/000030 | D.F.ZN35500/000030 | 0 | Carlingford | TOP RYDE |  | 400 | 1.8765 | 98.4929
D.F.ZN35500/00031L | D.F.ZN35500/000031 | 0 | Carlingford | TOP RYDE |  | 400 | 2.4533 | 128.7634
D.F.ZN35500/00031R | D.F.ZN35500/000031 | 1 | Carlingford | TOP RYDE |  | 295 | 1.8551 | 97.3655
D.F.ZN35500/000032 | D.F.ZN35500/000032 | 0 | Carlingford | TOP RYDE |  | 355 | 3.1116 | 163.3184
D.F.ZN35500/00034L | D.F.ZN35500/000034 | 0 | Carlingford | TOP RYDE |  | 400 | 1.7422 | 91.4392
D.F.ZN35500/000035 | D.F.ZN35500/000035 | 0 | Carlingford | TOP RYDE |  | 375 | 1.8086 | 94.9255
D.F.ZN35500/00036L | D.F.ZN35500/000036 | 0 | Carlingford | TOP RYDE |  | 350 | 3.8451 | 201.8152
D.F.ZN35555/000002 | D.F.ZN35555/000002 | 0 | Inner West Sydney | CROYDON |  | 315 | 3.7203 | 195.2644
D.F.ZN35555/000003 | D.F.ZN35555/000003 | 0 | Inner West Sydney | CROYDON |  | 325 | 3.7309 | 195.8227
D.F.ZN35555/000005 | D.F.ZN35555/000005 | 0 | Inner West Sydney | CROYDON |  | 400 | 1.9306 | 101.3295
D.F.ZN35555/000006 | D.F.ZN35555/000006 | 0 | Inner West Sydney | CROYDON |  | 320 | 2.5913 | 136.0054
D.F.ZN35555/000008 | D.F.ZN35555/000008 | 0 | Inner West Sydney | CROYDON |  | 400 | 2.0989 | 110.1649
D.F.ZN35555/000009 | D.F.ZN35555/000009 | 0 | Inner West Sydney | CROYDON |  | 315 | 2.1278 | 111.6783
D.F.ZN35555/000013 | D.F.ZN35555/000013 | 0 | Inner West Sydney | CROYDON |  | 315 | 3.8192 | 200.4574
D.F.ZN35555/000014 | D.F.ZN35555/000014 | 0 | Inner West Sydney | CROYDON |  | 325 | 1.674 | 87.861
D.F.ZN35555/000016 | D.F.ZN35555/000016 | 0 | Inner West Sydney | CROYDON |  | 260 | 2.0393 | 107.0363
D.F.ZN35555/000017 | D.F.ZN35555/000017 | 0 | Inner West Sydney | CROYDON |  | 315 | 3.4511 | 181.1354
D.F.ZN35555/000019 | D.F.ZN35555/000019 | 0 | Inner West Sydney | CROYDON |  | 330 | 3.4582 | 181.511
D.F.ZN35555/000020 | D.F.ZN35555/000020 | 0 | Inner West Sydney | CROYDON |  | 400 | 3.7783 | 198.3081
D.F.ZN35600/00001R | D.F.ZN35600/000001 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 330 | 3.4064 | 178.7894
D.F.ZN35600/00001L | D.F.ZN35600/000001 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 205 | 2.0516 | 107.6813
D.F.ZN35600/000002 | D.F.ZN35600/000002 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 205 | 1.853 | 97.2586
D.F.ZN35600/00003L | D.F.ZN35600/000003 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 2.7285 | 143.2067
D.F.ZN35600/00003R | D.F.ZN35600/000003 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 0.9348 | 49.0632
D.F.ZN35600/000004 | D.F.ZN35600/000004 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 355 | 2.2851 | 119.9392
D.F.ZN35600/00006R | D.F.ZN35600/000006 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 4.0735 | 213.8034
D.F.ZN35600/00006L | D.F.ZN35600/000006 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 2.803 | 147.1205
D.F.ZN35600/000007 | D.F.ZN35600/000007 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 300 | 1.9401 | 101.8268
D.F.ZN35600/00009R | D.F.ZN35600/000009 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 2.8138 | 147.6882
D.F.ZN35600/00009L | D.F.ZN35600/000009 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 205 | 2.3374 | 122.6836
D.F.ZN35600/000010 | D.F.ZN35600/000010 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 305 | 1.8963 | 99.5293
D.F.ZN35600/00011R | D.F.ZN35600/000011 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 3.172 | 166.4892
D.F.ZN35600/00012R | D.F.ZN35600/000012 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 2.8008 | 147.0039
D.F.ZN35600/00012L | D.F.ZN35600/000012 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 1.6889 | 88.6462
D.F.ZN35600/00014L | D.F.ZN35600/000014 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 290 | 3.2956 | 172.9751
D.F.ZN35600/00016L | D.F.ZN35600/000016 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 355 | 2.6772 | 140.5143
D.F.ZN35600/00016R | D.F.ZN35600/000016 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 265 | 0.7567 | 39.7184
D.F.ZN35600/000017 | D.F.ZN35600/000017 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 290 | 9.1064 | 477.9616
D.F.ZN35600/00019L | D.F.ZN35600/000019 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 4.527 | 237.6035
D.F.ZN35600/000020 | D.F.ZN35600/000020 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 295 | 0.7565 | 39.7072
D.F.ZN35600/00022R | D.F.ZN35600/000022 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 4.975 | 261.1183
D.F.ZN35600/00022L | D.F.ZN35600/000022 | 1 | Eastern Suburbs Outer | KINGSFORD |  | 265 | 2.8023 | 147.0824
D.F.ZN35600/00024R | D.F.ZN35600/000024 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 400 | 0.9908 | 52.0028
D.F.ZN35600/00025L | D.F.ZN35600/000025 | 0 | Eastern Suburbs Outer | KINGSFORD |  | 345 | 3.014 | 158.1956
D.F.ZN35700/00001L | D.F.ZN35700/000001 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 1.6933 | 88.8747
D.F.ZN35700/000002 | D.F.ZN35700/000002 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 295 | 0.426 | 22.3592
D.F.ZN35700/000004 | D.F.ZN35700/000004 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 300 | 4.262 | 223.697
D.F.ZN35700/000008 | D.F.ZN35700/000008 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 3.4033 | 178.6277
D.F.ZN35700/00009L | D.F.ZN35700/000009 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 0.4014 | 21.0673
D.F.ZN35700/00009R | D.F.ZN35700/000009 | 1 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 0.4014 | 21.0673
D.F.ZN35700/000010 | D.F.ZN35700/000010 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 1.7252 | 90.5505
D.F.ZN35700/00012L | D.F.ZN35700/000012 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 2.3561 | 123.6642
D.F.ZN35700/000013 | D.F.ZN35700/000013 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 275 | 2.9855 | 156.6992
D.F.ZN35700/00014L | D.F.ZN35700/000014 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 2.4105 | 126.5186
D.F.ZN35700/000019 | D.F.ZN35700/000019 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 0.382 | 20.0513
D.F.ZN35700/00020L | D.F.ZN35700/000020 | 0 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 0.4468 | 23.4516
D.F.ZN35700/00020R | D.F.ZN35700/000020 | 1 | Eastern Suburbs Outer | PORT BOTANY |  | 400 | 0.4466 | 23.441
D.F.ZN35800/00001L | D.F.ZN35800/000001 | 0 | Canterbury Bankstown | BANKSTOWN |  | 350 | 3.0298 | 159.0214
D.F.ZN35800/00001R | D.F.ZN35800/000001 | 1 | Canterbury Bankstown | BANKSTOWN |  |  |  | 0
D.F.ZN35800/000002 | D.F.ZN35800/000002 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 2.8071 | 147.3336
D.F.ZN35800/000003 | D.F.ZN35800/000003 | 0 | Canterbury Bankstown | BANKSTOWN |  | 295 | 2.7573 | 144.7197
D.F.ZN35800/000004 | D.F.ZN35800/000004 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 2.0314 | 106.6195
D.F.ZN35800/00006L | D.F.ZN35800/000006 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 2.0543 | 107.8225
D.F.ZN35800/000007 | D.F.ZN35800/000007 | 0 | Canterbury Bankstown | BANKSTOWN |  | 350 | 2.822 | 148.117
D.F.ZN35800/00009L | D.F.ZN35800/000009 | 0 | Canterbury Bankstown | BANKSTOWN |  | 280 | 1.0974 | 57.5984
D.F.ZN35800/000010 | D.F.ZN35800/000010 | 0 | Canterbury Bankstown | BANKSTOWN |  | 300 | 3.3194 | 174.2237
D.F.ZN35800/000011 | D.F.ZN35800/000011 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 1.8018 | 94.5717
D.F.ZN35800/00013L | D.F.ZN35800/000013 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 3.0234 | 158.6848
D.F.ZN35800/00013R | D.F.ZN35800/000013 | 1 | Canterbury Bankstown | BANKSTOWN |  |  |  | 0
D.F.ZN35800/000014 | D.F.ZN35800/000014 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 5.5162 | 289.5234
D.F.ZN35800/00015L | D.F.ZN35800/000015 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 2.6968 | 141.5453
D.F.ZN35800/000016 | D.F.ZN35800/000016 | 0 | Canterbury Bankstown | BANKSTOWN |  | 295 | 4.2239 | 221.697
D.F.ZN35800/00018L | D.F.ZN35800/000018 | 0 | Canterbury Bankstown | BANKSTOWN |  | 305 | 3.8696 | 203.1019
D.F.ZN35800/000019 | D.F.ZN35800/000019 | 0 | Canterbury Bankstown | BANKSTOWN |  | 350 | 1.9824 | 104.0467
D.F.ZN35800/00021L | D.F.ZN35800/000021 | 0 | Canterbury Bankstown | BANKSTOWN |  | 400 | 1.1249 | 59.0395
D.F.ZN35800/000022 | D.F.ZN35800/000022 | 0 | Canterbury Bankstown | BANKSTOWN |  | 330 | 3.3225 | 174.3857
D.F.ZN35900/00001L | D.F.ZN35900/000001 | 0 | Canterbury Bankstown | POTTS HILL |  | 295 | 3.1264 | 164.0909
D.F.ZN35900/00002L | D.F.ZN35900/000002 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 3.1698 | 166.3701
D.F.ZN35900/000003 | D.F.ZN35900/000003 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 3.6201 | 190.0077
D.F.ZN35900/00004L | D.F.ZN35900/000004 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 2.855 | 149.8484
D.F.ZN35900/000006 | D.F.ZN35900/000006 | 0 | Canterbury Bankstown | POTTS HILL |  | 390 | 1.7068 | 89.5844
D.F.ZN35900/00007L | D.F.ZN35900/000007 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 1.1664 | 61.222
D.F.ZN35900/00010L | D.F.ZN35900/000010 | 0 | Canterbury Bankstown | POTTS HILL |  | 400 | 2.4709 | 129.6876
D.F.ZN35900/000011 | D.F.ZN35900/000011 | 0 | Canterbury Bankstown | POTTS HILL |  | 320 | 2.2884 | 120.1082
D.F.ZN35900/00012L | D.F.ZN35900/000012 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 2.226 | 116.8347
D.F.ZN35900/00014L | D.F.ZN35900/000014 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 2.0132 | 105.666
D.F.ZN35900/00015L | D.F.ZN35900/000015 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 0.9522 | 49.9752
D.F.ZN35900/000016 | D.F.ZN35900/000016 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 1.7605 | 92.4033
D.F.ZN35900/00017L | D.F.ZN35900/000017 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 3.5122 | 184.343
D.F.ZN35900/00020L | D.F.ZN35900/000020 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 2.3973 | 125.8258
D.F.ZN35900/000022 | D.F.ZN35900/000022 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 1.5133 | 79.4285
D.F.ZN35900/00023L | D.F.ZN35900/000023 | 0 | Canterbury Bankstown | POTTS HILL |  | 320 | 1.2506 | 65.6383
D.F.ZN35900/000024 | D.F.ZN35900/000024 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 3.499 | 183.6493
D.F.ZN35900/00025L | D.F.ZN35900/000025 | 0 | Canterbury Bankstown | POTTS HILL |  | 350 | 1.6851 | 88.4434
D.F.ZN36000/000001 | D.F.ZN36000/000001 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 2.2445 | 117.804
D.F.ZN36000/00002L | D.F.ZN36000/000002 | 0 | Inner West Sydney | OLYMPIC PARK |  | 380 | 1.8714 | 98.2249
D.F.ZN36000/000004 | D.F.ZN36000/000004 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 3.6953 | 193.9542
D.F.ZN36000/000006 | D.F.ZN36000/000006 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 3.5052 | 183.9762 | 1
D.F.ZN36000/000007 | D.F.ZN36000/000007 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 5.1644 | 271.0588
D.F.ZN36000/000008 | D.F.ZN36000/000008 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 2.983 | 156.5667
D.F.ZN36000/000010 | D.F.ZN36000/000010 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 2.0657 | 108.4192 | 1
D.F.ZN36000/00012L | D.F.ZN36000/000012 | 0 | Inner West Sydney | OLYMPIC PARK |  | 380 | 2.9285 | 153.7078
D.F.ZN36000/000017 | D.F.ZN36000/000017 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 1.6303 | 85.5703
D.F.ZN36000/000019 | D.F.ZN36000/000019 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 2.0816 | 109.2555
D.F.ZN36000/000022 | D.F.ZN36000/000022 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 1.095 | 57.473
D.F.ZN36000/000024 | D.F.ZN36000/000024 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 3.9786 | 208.8229
D.F.ZN36000/000025 | D.F.ZN36000/000025 | 0 | Inner West Sydney | OLYMPIC PARK |  | 320 | 1.1715 | 61.4899
D.F.ZN36000/000026 | D.F.ZN36000/000026 | 0 | Inner West Sydney | OLYMPIC PARK |  | 400 | 3.2326 | 169.6682
D.F.ZN36100/00001L | D.F.ZN36100/000001 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 290 | 2.5305 | 132.818
D.F.ZN36100/000002 | D.F.ZN36100/000002 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 400 | 3.157 | 165.6997
D.F.ZN36100/000005 | D.F.ZN36100/000005 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 265 | 3.4044 | 178.6847
D.F.ZN36100/00006L | D.F.ZN36100/000006 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 400 | 3.9044 | 204.9303
D.F.ZN36100/000007 | D.F.ZN36100/000007 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 295 | 1.4299 | 75.05
D.F.ZN36100/00008L | D.F.ZN36100/000008 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 300 | 2.8308 | 148.5804
D.F.ZN36100/000009 | D.F.ZN36100/000009 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 400 | 1.3695 | 71.8781
D.F.ZN36100/00012L | D.F.ZN36100/000012 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 305 | 3.3214 | 174.3264
D.F.ZN36100/00013L | D.F.ZN36100/000013 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 290 | 3.7137 | 194.9188
D.F.ZN36100/00015L | D.F.ZN36100/000015 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 305 | 2.1629 | 113.5239
D.F.ZN36100/000016 | D.F.ZN36100/000016 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 370 | 1.5543 | 81.5811
D.F.ZN36100/000019 | D.F.ZN36100/000019 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 290 | 3.391 | 177.9836
D.F.ZN36100/00020L | D.F.ZN36100/000020 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 400 | 2.465 | 129.3791
D.F.ZN36100/000021 | D.F.ZN36100/000021 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 308 | 2.8729 | 150.7903
D.F.ZN36100/000023 | D.F.ZN36100/000023 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 295 | 2.202 | 115.5749
D.F.ZN36100/00025L | D.F.ZN36100/000025 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 265 | 3.8033 | 199.623
D.F.ZN36100/00026L | D.F.ZN36100/000026 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 280 | 2.2055 | 115.7584
D.F.ZN36100/00027L | D.F.ZN36100/000027 | 0 | Eastern Suburbs Outer | ROSE BAY |  | 290 | 2.6215 | 137.5909
D.F.ZN36200/00001L | D.F.ZN36200/000001 | 0 | Lower Central Coast | EMPIRE BAY |  | 400 | 3.5991 | 188.9027
D.F.ZN36200/00001R | D.F.ZN36200/000001 | 1 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/000003 | D.F.ZN36200/000003 | 0 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/000004 | D.F.ZN36200/000004 | 0 | Lower Central Coast | EMPIRE BAY |  | 400 | 2.6751 | 140.4071
D.F.ZN36200/00005L | D.F.ZN36200/000005 | 0 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/00005R | D.F.ZN36200/000005 | 1 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/00007L | D.F.ZN36200/000007 | 0 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/00007R | D.F.ZN36200/000007 | 1 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/000008 | D.F.ZN36200/000008 | 0 | Lower Central Coast | EMPIRE BAY |  | 400 | 3.3465 | 175.6459
D.F.ZN36200/000009 | D.F.ZN36200/000009 | 0 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36200/00011L | D.F.ZN36200/000011 | 0 | Lower Central Coast | EMPIRE BAY |  | 400 | 2.9573 | 155.2182
D.F.ZN36200/00011R | D.F.ZN36200/000011 | 1 | Lower Central Coast | EMPIRE BAY |  |  |  | 0
D.F.ZN36300/00001L | D.F.ZN36300/000001 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 1.5235 | 79.9631
D.F.ZN36300/000003 | D.F.ZN36300/000003 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 5.0247 | 263.7281
D.F.ZN36300/00005L | D.F.ZN36300/000005 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 350 | 3.5075 | 184.0978
D.F.ZN36300/000007 | D.F.ZN36300/000007 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 0.7758 | 40.7187
D.F.ZN36300/00008L | D.F.ZN36300/000008 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 350 | 2.2 | 115.4685
D.F.ZN36300/000009 | D.F.ZN36300/000009 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 3.0118 | 158.0778
D.F.ZN36300/00011L | D.F.ZN36300/000011 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 280 | 2.4902 | 130.7016
D.F.ZN36300/00012L | D.F.ZN36300/000012 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 295 | 4.0451 | 212.3127
D.F.ZN36300/000013 | D.F.ZN36300/000013 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 1.091 | 57.2614
D.F.ZN36300/000017 | D.F.ZN36300/000017 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 1.9633 | 103.0459
D.F.ZN36300/00018L | D.F.ZN36300/000018 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 400 | 2.2016 | 115.5528
D.F.ZN36300/000019 | D.F.ZN36300/000019 | 0 | Manly Warringah | BALGOWLAH NORTH |  | 360 | 3.6923 | 193.7966
D.F.ZN36800/00031R | D.F.ZN36800/000031 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 3.2817 | 172.2427
D.F.ZN36800/00031L | D.F.ZN36800/000031 | 1 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 2.5527 | 133.9803
D.F.ZN36800/000032 | D.F.ZN36800/000032 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 305 | 0.5882 | 30.8702
D.F.ZN36800/000033 | D.F.ZN36800/000033 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 2.1108 | 110.7871
D.F.ZN36800/000035 | D.F.ZN36800/000035 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 295 | 3.0737 | 161.3258
D.F.ZN36800/000036 | D.F.ZN36800/000036 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 1.7134 | 89.9295
D.F.ZN36800/00039L | D.F.ZN36800/000039 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 3.2417 | 170.1438
D.F.ZN36800/000040 | D.F.ZN36800/000040 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 5.389 | 282.8484
D.F.ZN36800/000042 | D.F.ZN36800/000042 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 305 | 1.138 | 59.7289
D.F.ZN36800/000043 | D.F.ZN36800/000043 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 295 | 3.4527 | 181.2215
D.F.ZN36800/00046L | D.F.ZN36800/000046 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 1.7831 | 93.5877
D.F.ZN36800/000047 | D.F.ZN36800/000047 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 320 | 0.2274 | 11.9357
D.F.ZN36800/000049 | D.F.ZN36800/000049 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 305 | 2.0478 | 107.4804
D.F.ZN36800/000050 | D.F.ZN36800/000050 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 215 | 2.5168 | 132.0969
D.F.ZN36800/00053R | D.F.ZN36800/000053 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 1.6221 | 85.1369
D.F.ZN36800/000054 | D.F.ZN36800/000054 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 3.066 | 160.9241
D.F.ZN36800/000056 | D.F.ZN36800/000056 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 2.2412 | 117.6312
D.F.ZN36800/000057 | D.F.ZN36800/000057 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 0.4425 | 23.2242
D.F.ZN36800/000058 | D.F.ZN36800/000058 | 0 | Eastern Suburbs Outer | WAVERLEY |  | 400 | 3.9231 | 205.908
D.F.ZN37100/000002 | D.F.ZN37100/000002 | 0 | Canterbury Bankstown | GREENACRE |  | 390 |  | 0
D.F.ZN37100/000004 | D.F.ZN37100/000004 | 0 | Canterbury Bankstown | GREENACRE |  | 390 | 3.7897 | 198.9099
D.F.ZN37100/000005 | D.F.ZN37100/000005 | 0 | Canterbury Bankstown | GREENACRE |  | 310 | 3.7592 | 197.3083
D.F.ZN37100/000006 | D.F.ZN37100/000006 | 0 | Canterbury Bankstown | GREENACRE |  | 385 | 5.1503 | 270.322
D.F.ZN37100/000008 | D.F.ZN37100/000008 | 0 | Canterbury Bankstown | GREENACRE |  | 400 | 3.7192 | 195.2094
D.F.ZN37100/000009 | D.F.ZN37100/000009 | 0 | Canterbury Bankstown | GREENACRE |  | 340 | 3.035 | 159.2984
D.F.ZN37100/000010 | D.F.ZN37100/000010 | 0 | Canterbury Bankstown | GREENACRE |  | 400 | 3.2554 | 170.8652
D.F.ZN37100/000011 | D.F.ZN37100/000011 | 0 | Canterbury Bankstown | GREENACRE |  | 300 | 3.3308 | 174.8224
D.F.ZN37100/000013 | D.F.ZN37100/000013 | 0 | Canterbury Bankstown | GREENACRE |  | 400 |  | 0
D.F.ZN37100/000015 | D.F.ZN37100/000015 | 0 | Canterbury Bankstown | GREENACRE |  | 400 | 3.6409 | 191.0955
D.F.ZN37100/000016 | D.F.ZN37100/000016 | 0 | Canterbury Bankstown | GREENACRE |  | 390 | 1.6207 | 85.0636
D.F.ZN37100/000017 | D.F.ZN37100/000017 | 0 | Canterbury Bankstown | GREENACRE |  | 350 | 3.2224 | 169.1343
D.F.ZN37100/000024 | D.F.ZN37100/000024 | 0 | Canterbury Bankstown | GREENACRE |  | 400 | 4.2418 | 222.6381
D.F.ZN37100/000025 | D.F.ZN37100/000025 | 0 | Canterbury Bankstown | GREENACRE |  | 350 | 3.5959 | 188.7382
D.F.ZN37100/000026 | D.F.ZN37100/000026 | 0 | Canterbury Bankstown | GREENACRE |  | 340 | 0.3556 | 18.6616
D.F.ZN37100/000030 | D.F.ZN37100/000030 | 0 | Canterbury Bankstown | GREENACRE |  | 400 | 3.2923 | 172.7987
D.F.ZN37100/000031 | D.F.ZN37100/000031 | 0 | Canterbury Bankstown | GREENACRE |  | 350 | 4.0818 | 214.2408
D.F.ZN37100/000033 | D.F.ZN37100/000033 | 0 | Canterbury Bankstown | GREENACRE |  | 340 | 2.9377 | 154.1917
D.F.ZN37100/000035 | D.F.ZN37100/000035 | 0 | Canterbury Bankstown | GREENACRE |  | 400 |  | 0
D.F.ZN37100/000036 | D.F.ZN37100/000036 | 0 | Canterbury Bankstown | GREENACRE |  | 310 | 1.0465 | 54.9295
D.F.ZN37100/000038 | D.F.ZN37100/000038 | 0 | Canterbury Bankstown | GREENACRE |  | 385 | 4.1018 | 215.2887
D.F.ZN37100/000039 | D.F.ZN37100/000039 | 0 | Canterbury Bankstown | GREENACRE |  | 400 | 0.8711 | 45.7187
D.F.ZN37100/000040 | D.F.ZN37100/000040 | 0 | Canterbury Bankstown | GREENACRE |  | 340 | 4.3837 | 230.082
D.F.ZN37300/000002 | D.F.ZN37300/000002 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 3.3857 | 177.7022
D.F.ZN37300/000003 | D.F.ZN37300/000003 | 0 | Canterbury Bankstown | SUMMER HILL |  | 350 | 1.1929 | 62.6104
D.F.ZN37300/000005 | D.F.ZN37300/000005 | 0 | Canterbury Bankstown | SUMMER HILL |  | 305 | 3.3023 | 173.3281
D.F.ZN37300/000006 | D.F.ZN37300/000006 | 0 | Canterbury Bankstown | SUMMER HILL |  | 400 | 2.9584 | 155.2779
D.F.ZN37300/000007 | D.F.ZN37300/000007 | 0 | Canterbury Bankstown | SUMMER HILL |  | 390 | 0.2823 | 14.8171
D.F.ZN37300/000010 | D.F.ZN37300/000010 | 0 | Canterbury Bankstown | SUMMER HILL |  | 400 | 2.0423 | 107.1912
D.F.ZN37300/000011 | D.F.ZN37300/000011 | 0 | Canterbury Bankstown | SUMMER HILL |  | 305 | 2.2071 | 115.8429
D.F.ZN37300/000012 | D.F.ZN37300/000012 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 4.1978 | 220.3289
D.F.ZN37300/000014 | D.F.ZN37300/000014 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 2.5104 | 131.7603
D.F.ZN37300/000015 | D.F.ZN37300/000015 | 0 | Canterbury Bankstown | SUMMER HILL |  | 335 | 2.5195 | 132.2394
D.F.ZN37300/000018 | D.F.ZN37300/000018 | 0 | Canterbury Bankstown | SUMMER HILL |  | 400 | 1.0635 | 55.8175
D.F.ZN37300/000019 | D.F.ZN37300/000019 | 0 | Canterbury Bankstown | SUMMER HILL |  | 325 | 3.3149 | 173.9848
D.F.ZN37300/000020 | D.F.ZN37300/000020 | 0 | Canterbury Bankstown | SUMMER HILL |  | 335 | 2.8952 | 151.9578
D.F.ZN37300/000021 | D.F.ZN37300/000021 | 0 | Canterbury Bankstown | SUMMER HILL |  | 360 | 1.8268 | 95.8796
D.F.ZN37300/000022 | D.F.ZN37300/000022 | 0 | Canterbury Bankstown | SUMMER HILL |  | 390 | 1.4702 | 77.1659
D.F.ZN37300/000025 | D.F.ZN37300/000025 | 0 | Canterbury Bankstown | SUMMER HILL |  | 305 | 2.9107 | 152.7734
D.F.ZN37300/000026 | D.F.ZN37300/000026 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 2.4482 | 128.4989
D.F.ZN37300/000027 | D.F.ZN37300/000027 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 3.1826 | 167.0442
D.F.ZN37300/000029 | D.F.ZN37300/000029 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 2.7818 | 146.0072
D.F.ZN37300/000030 | D.F.ZN37300/000030 | 0 | Canterbury Bankstown | SUMMER HILL |  | 320 | 0.405 | 21.2568