## System Limitations DAPR
System Limitations DAPR
Substation/Feeder Name | Peak season | Constraint primary driver | Location of constraint (start) Latitude | Location of constraint (start) Longtitude | Location of constraint (end) Latitude | Location of constraint (end) Longtitude | Asset ID | Network Element | Residential customers affected | Residential customers affected (%) | Asset rating (MVA) S25/26 or W26 | Asset rating (MVA) S26/27 or W27 | Asset rating (MVA) S27/28 or W28 | Asset rating (MVA) S28/29 or W29 | Asset rating (MVA) S29/30 or W30 | Asset rating (MW) S25/26 or W26 | Asset rating (MW) S26/27 or W27 | Asset rating (MW) S27/28 or W28 | Asset rating (MW) S28/29 or W29 | Asset rating (MW) S29/30 or W30 | Forecast Demand POE50 (MVA) S25/26 or W26 | Forecast Demand POE50 (MVA) S26/27 or W27 | Forecast Demand POE50 (MVA) S27/28 or W28 | Forecast Demand POE50 (MVA) S28/29 or W29 | Forecast Demand POE50 (MVA) S29/30 or W30 | Forecast Demand POE10 (MVA) S25/26 or W26 | Forecast Demand POE10 (MVA) S26/27 or W27 | Forecast Demand POE10 (MVA) S27/28 or W28 | Forecast Demand POE10 (MVA) S28/29 or W29 | Forecast Demand POE10 (MVA) S29/30 or W30 | Forecast Demand POE50 (MW) S25/26 or W26 | Forecast Demand POE50 (MW) S26/27 or W27 | Forecast Demand POE50 (MW) S27/28 or W28 | Forecast Demand POE50 (MW) S28/29 or W29 | Forecast Demand POE50 (MW) S29/30 or W30 | Forecast Demand POE10 (MW) S25/26 or W26 | Forecast Demand POE10 (MW) S26/27 or W27 | Forecast Demand POE10 (MW) S27/28 or W28 | Forecast Demand POE10 (MW) S28/29 or W29 | Forecast Demand POE10 (MW) S29/30 or W30 | Voltage level | Maximum Load at risk (MW) S25/26 or W26 | Maximum Load at risk (MW) S26/27 or W27 | Maximum Load at risk (MW) S27/28 or W28 | Maximum Load at risk (MW) S28/29 or W29 | Maximum Load at risk (MW) S29/30 or W30 | Energy at risk (MWh) S25/26 or W26 | Energy at risk (MWh) S26/27 or W27 | Energy at risk (MWh) S27/28 or W28 | Energy at risk (MWh) S28/29 or W29 | Energy at risk (MWh) S29/30 or W30 | Preferred network investment | Preferred network investment capital cost ($M REAL) | Preferred network investment operating cost ($M REAL) | Preferred network investment cost accuracy (+ %) | Preferred network investment cost accuracy (- %) | Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Demand reduction required to defer investment by 1 year (MW) | Annual Deferral Value ($M) | Load transfer capability (MVA) | Load transfer capability (MW) | Emergency generation | Historic use of existing emergency resonponse | Project Index | Representative Interval Data | pf
Fdr 386 Surry Hills STS - Darlinghurst Tx 4 | Summer | Asset condition - 33kV feeder | -33.8825 | 151.2122 | -33.8781 | 151.2176 | Fdr 386 | Sub-transmission line | 7048 | 84% | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 26.5446 | 26.5446 | 26.5446 | 26.5446 | 26.5446 | 28.3938 | 28.3551 | 28.0672 | 27.9254 | 27.9135 | NA | NA | NA | NA | NA | 27.8118 | 27.7739 | 27.4919 | 27.3531 | 27.3414 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | 4.2265 | 6.07 | 8.0517 | 10.6417 | 13.9926 | Replace 33kV gas feeders 386 and 389 | 8.3 | 0.0415 | 20% | 10% | 2028-03-01 | 2 | 1.959 | 0.29614 | 13.8475 | 13.5637 | NA | NA | 2 | Darlinghurst 33/11kV | 0.9795
Fdr 389 Surry Hills STS - Darlinghurst Tx 3 | Summer | Asset condition - 33kV feeder | -33.8825 | 151.2122 | -33.8781 | 151.2176 | Fdr 389 | Sub-transmission line |  |  | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 26.5446 | 26.5446 | 26.5446 | 26.5446 | 26.5446 | 28.4305 | 28.3913 | 28.1024 | 27.9607 | 27.9478 | NA | NA | NA | NA | NA | 27.8478 | 27.8094 | 27.5265 | 27.3876 | 27.375 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 386 Surry Hills STS - Darlinghurst Tx4 |  |  |  |  | Replace 33kV gas feeders 386 and 389 |  |  | 20% | 10% |  |  |  |  | Combined with Fdr 386 Surry Hills STS - Darlinghurst Tx4 |  | NA | NA | 2 | Darlinghurst 33/11kV | 0.9795
Botany ZS | Summer | Asset condition - 11kV switchgear | -33.9476 | 151.2045 | -33.9476 | 151.2045 | ZN340 | Zone Substation | 8498 | 87% | 33 | 33 | 33 | 33 | 33 | 32.5472 | 32.5472 | 32.5472 | 32.5472 | 32.5472 | 30.0513 | 30.5218 | 30.444 | 30.4232 | 32.1579 | 31.6857 | 32.0936 | 31.9525 | 31.876 | 33.608 | 29.639 | 30.103 | 30.0263 | 30.0058 | 31.7167 | 31.251 | 31.6533 | 31.5142 | 31.4387 | 33.1469 | 11kV | 0 | 0 | 0 | 0 | 0 | 4.1031 | 4.4242 | 4.6762 | 4.9553 | 5.6162 | Replace 11kV compound switchgear at Botany zone substation | 10 | 0.05 | 20% | 10% | 2029-02-01 | 6 | 5.9177 | 0.3568 | 10.3518 | 10.2097 | NA | NA | 3 | Botany 33/11kV | 0.98628
Willoughby STS | Summer | Asset Condition - 33kV switchgear | -33.8171 | 151.1855 | -33.8171 | 151.1855 | TS7220 | Sub-transmission Substation | 24798 | 88% | 225.4 | 225.4 | 225.4 | 225.4 | 225.4 | 223.0446 | 223.0446 | 223.0446 | 223.0446 | 223.0446 | 156.2 | 189.66 | 200.87 | 211.63 | 222.21 | 168.95 | 202.46 | 213.47 | 224.21 | 235.2 | 154.5677 | 187.6781 | 198.7709 | 209.4185 | 219.8879 | 168.95 | 202.46 | 213.48 | 224.21 | 235.2 | 33kV | 0 | 0 | 0 | 0 | 0 | 7.73 | 6.65 | 9.2 | 12.11 | 13.5 | Replacement of 33kV switchgear at Willoughby STS | 70 | 0.35 | 20% | 10% | 2032-04-01 | NA | NA | 2.4976 | 17.5 | 17.3171 | NA | NA | 4 | Willoughby 132/33kV | 0.98955
Merewether STS | Summer | Asset Condition - 33kV switchgear | -32.9351 | 151.7365 | -32.9351 | 151.7365 | TS00405 | Sub-transmission Substation | 48222 | 88% | 274.4 | 274.4 | 274.4 | 274.4 | 274.4 | 266.168 | 266.168 | 266.168 | 266.168 | 266.168 | 187.51 | 187.9 | 190.69 | 189.22 | 191.97 | 198.19 | 199.63 | 202.6 | 201.21 | 204.31 | 181.8847 | 182.263 | 184.9693 | 183.5434 | 186.2109 | 192.2443 | 193.6411 | 196.522 | 195.1737 | 198.1807 | 33kV | 0 | 0 | 0 | 0 | 0 | 0.63 | 0.63 | 0.65 | 0.66 | 0.67 | Replacement of 33kV switchgear at Merewether STS | 47.1 | 0.2355 | 30% | 10% | 2030-09-01 | NA | NA | 1.6805 | 30.2 | 29.294 | NA | NA | 5 | Merewether 13233kV | 0.97
Blakehurst ZS | Summer | Asset condition - 11kV switchgear | -33.977 | 151.1155 | -33.977 | 151.1155 | ZN10991 | Zone Substation | 11773 | 94% | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 30.9133 | 30.9133 | 30.9133 | 30.9133 | 30.9133 | 24.2929 | 26.0028 | 26.1191 | 26.2047 | 26.2165 | 26.83 | 28.77 | 29.05 | 29.38 | 29.61 | 23.7651 | 25.4377 | 25.5515 | 25.6353 | 25.6468 | 26.247 | 28.1448 | 28.4187 | 28.7416 | 28.9666 | 11kV | 12.8708 | 14.5435 | 14.6572 | 14.741 | 14.7525 | 4.7 | 5.09 | 5.47 | 5.86 | 6.25 | Transfer all load to Kogarah zone substation and decommission Blakehurst zone substation and associated 33kV gas cables | 22.7 | 0.1135 | 30% | 10% | 2029-09-01 | 3 | 2.9348 | 0.80993 | 11.1363 | 10.8943 | NA | NA | 6 | Blakehurst 33/11kV | 0.97827
Fdr 769 Peakhurst STS - Blakehurst | Summer | Asset Condition - 33kV feeder | -33.9659 | 151.0626 | -33.977 | 151.1155 | Fdr 769 | Sub-transmission line |  |  | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.3155 | 26.3155 | 26.3155 | 26.3155 | 26.3155 | 22.8799 | 24.0177 | 23.282 | 22.8949 | 22.5793 | NA | NA | NA | NA | NA | 22.3827 | 23.4958 | 22.7761 | 22.3974 | 22.0887 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | 2.51 | 3.48 | 3.82 | 4.17 | 4.51 | [9 empty] | 11.1363 | 10.8943 | NA | NA | 6 | Blakehurst 33/11kV | 0.97827
Fdr 770 Peakhurst STS - Blakehurst | Summer | Asset Condition - 33kV feeder | -33.9659 | 151.0626 | -33.977 | 151.1155 | Fdr 770 | Sub-transmission line |  |  | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.2176 | 26.2176 | 26.2176 | 26.2176 | 26.2176 | 22.8799 | 24.0178 | 23.282 | 22.8949 | 22.5794 | NA | NA | NA | NA | NA | 22.3827 | 23.4959 | 22.7761 | 22.3974 | 22.0887 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 769 Peakhurst STS - Blakehurst | [13 empty] | 11.1363 | 10.8943 | NA | NA | 6 | Blakehurst 33/11kV | 0.97827
`

## System Limitations TAPR - STS
System Limitations TAPR - STS
Connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point (Latitude) | Constrained connection point (Longitude) | Annual energy of residential customers affected (MWh) | Peak demand of residential customers affected (MW) | Annual energy of industrial customers affected (MWh) | Peak demand of industrial customers affected (MW) | Annual energy of commercial customers affected (MWh) | Peak demand of commercial customers affected (MW) | Forecast P50 Max Demand on max demand day (MVA) & S25/26 or W26 | Forecast P50 Max Demand on max demand day (MVA) & S26/27 or W27 | Forecast P50 Max Demand on max demand day (MVA) & S27/28 or W28 | Forecast P50 Max Demand on max demand day (MVA) & S28/29 or W29 | Forecast P50 Max Demand on max demand day (MVA) & S29/30 or W30 | Forecast P50 Max Demand on max demand day (MVA) & S30/31 or W31 | Forecast P50 Max Demand on max demand day (MVA) & S31/32 or W32 | Forecast P50 Max Demand on max demand day (MVA)& S32/33 or W33 | Forecast P50 Max Demand on max demand day (MVA)& S33/34 or W34 | Forecast P50 Max Demand on max demand day (MVA)& S34/35 or W35 | Forecast P10 Max Demand on max demand day (MVA) S25/26 or W26 | Forecast P10 Max Demand on max demand day (MVA) S26/27 or W27 | Forecast P10 Max Demand on max demand day (MVA) S27/28 or W28 | Forecast P10 Max Demand on max demand day (MVA) S28/29 or W29 | Forecast P10 Max Demand on max demand day (MVA) S29/30 or W30 | Forecast P10 Max Demand on max demand day (MVA) S30/31 or W31 | Forecast P10 Max Demand on max demand day (MVA) S31/32 or W32 | Forecast P10 Max Demand on max demand day (MVA) S32/33 or W33 | Forecast P10 Max Demand on max demand day (MVA) S33/34 or W34 | Forecast P10 Max Demand on max demand day (MVA) S34/35 or W35 | Forecast P50 Max Demand on min demand day (MW) S25/26 or W26 | Forecast P50 Max Demand on min demand day (MW) S26/27 or W27 | Forecast P50 Max Demand on min demand day (MW) S27/28 or W28 | Forecast P50 Max Demand on min demand day (MW) S28/29 or W29 | Forecast P50 Max Demand on min demand day (MW) S29/30 or W30 | Forecast P50 Max Demand on min demand day (MW) S30/31 or W31 | Forecast P50 Max Demand on min demand day (MW) S31/32 or W32 | Forecast P50 Max Demand on min demand day (MW) S32/33 or W33 | Forecast P50 Max Demand on min demand day (MW) S33/34 or W34 | Forecast P50 Max Demand on min demand day (MW) S34/35 or W35 | Forecast P10 Max Demand on min demand day (MW) S25/26 or W26 | Forecast P10 Max Demand on min demand day (MW) S26/27 or W27 | Forecast P10 Max Demand on min demand day (MW) S27/28 or W28 | Forecast P10 Max Demand on min demand day (MW) S28/29 or W29 | Forecast P10 Max Demand on min demand day (MW) S29/30 or W30 | Forecast P10 Max Demand on min demand day (MW) S30/31 or W31 | Forecast P10 Max Demand on min demand day (MW) S31/32 or W32 | Forecast P10 Max Demand on min demand day (MW) S32/33 or W33 | Forecast P10 Max Demand on min demand day (MW) S33/34 or W34 | Forecast P10 Max Demand on min demand day (MW) S34/35 or W35 | Voltage level (kV) | Maximum Load at risk per year (MVA) S25/26 or W26 | Maximum Load at risk per year (MVA) S26/27 or W27 | Maximum Load at risk per year (MVA) S27/28 or W28 | Maximum Load at risk per year (MVA) S28/29 or W29 | Maximum Load at risk per year (MVA) S29/30 or W30 | Maximum Load at risk per year (MVA) S30/31 or W31 | Maximum Load at risk per year (MVA) S31/32 or W32 | Maximum Load at risk per year (MVA) S32/33 or W33 | Maximum Load at risk per year (MVA) S33/34 or W34 | Maximum Load at risk per year (MVA) S34/35 or W35 | Maximum Load at risk per year (MW) S25/26 or W26 | Maximum Load at risk per year (MW) S26/27 or W27 | Maximum Load at risk per year (MW) S27/28 or W28 | Maximum Load at risk per year (MW) S28/29 or W29 | Maximum Load at risk per year (MW) S29/30 or W30 | Maximum Load at risk per year (MW) S30/31 or W31 | Maximum Load at risk per year (MW) S31/32 or W32 | Maximum Load at risk per year (MW) S32/33 or W33 | Maximum Load at risk per year (MW) S33/34 or W34 | Maximum Load at risk per year (MW) S34/35 or W35 | Preferred investment - Description | Preferred investment - Capital cost ($M REAL) | Preferred investment - Annual operating cost ($M REAL) | Preferred investment - Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Annual Deferral Value ($M REAL) | Load transfer capacity (MVA) | Historic connection point rating (MVA) S22/23 or W23 | Historic connection point rating (MVA) S23/24 or W24 | Historic connection point rating (MVA) S24/25 or W25 | Limitation asset | Unplanned outages | Maximum fault level (MVA) | Annual economic cost of constraint ($constant) S25/26 or W26 | Annual economic cost of constraint ($constant) S26/27 or W27 | Annual economic cost of constraint ($constant) S27/28 or W28 | Annual economic cost of constraint ($constant) S28/29 or W29 | Annual economic cost of constraint ($constant) S29/30 or W30 | Annual economic cost of constraint ($constant) S30/31 or W31 | Annual economic cost of constraint ($constant) S31/32 or W32 | Annual economic cost of constraint ($constant) S32/33 or W33 | Annual economic cost of constraint ($constant) S33/34 or W34 | Annual economic cost of constraint ($constant) S34/35 or W35 | VCR ($/MWh) | Annual EUE (MWh) S25/26 or W26 | Annual EUE (MWh) S26/27 or W27 | Annual EUE (MWh) S27/28 or W28 | Annual EUE (MWh) S28/29 or W29 | Annual EUE (MWh) S29/30 or W30 | Annual EUE (MWh) S30/31 or W31 | Annual EUE (MWh) S31/32 or W32 | Annual EUE (MWh) S32/33 or W33 | Annual EUE (MWh) S33/34 or W34 | Annual EUE (MWh) S34/35 or W35 | Project Index for additional data%
Wallumatta STS (Macquarie Park) | Load growth - Substation capacity and connection points |  | -33.7872 | 151.1323 | N/A | N/A | N/A | N/A | N/A | N/A | 96.05 | 156.4 | 233.75 | 312.8 | 366.35 | 433.5 | 484.5 | 536.35 | 553.35 | 581.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 132 | 0 | 45 | 110 | 181 | 219 | 278 | 321 | 379 | 395 | 416 | 0 | 45 | 110 | 181 | 219 | 278 | 321 | 379 | 395 | 416 | Establish New Wallumatta STS | 147.3 | 0.143 | +/-30% | 2029-06-01 | NA | 5.2556 | 0 | 0 | 0 | 0 | Transformer and 33kV switchgear | N/A | N/A | 0 | 0.01 | 10.96 | 3048.83 | 10250976.1 | 5631388194.86 | 24200369623.76 | 53156379670.41 | 64027190043.42 | 82683113520.71 | 52024 | 0 | 1.9222e-07 | 0.00021067 | 0.058604 | 197.0432 | 108245.9671 | 465177.0264 | 1021766.4861 | 1230724.0897 | 1589326.3402
Mascot East | Load growth - Substation capacity and connection points |  | -33.914409 | 151.1906 | [6 empty] | 0 | 0 | 0 | 21.3472 | 42.6944 | 64.0416 | 85.3888 | 99.6203 | 99.6203 | 99.6203 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [20 empty] | 132 | 0 | 0 | 0 | 21.3472 | 42.6944 | 64.0416 | 85.3888 | 99.6203 | 99.6203 | 99.6203 | 0 | 0 | 0 | 19.2125 | 38.425 | 57.6374 | 76.8499 | 89.6582 | 89.6582 | 89.6582 | Establish New Mascot East switching station | 55.9 | 0.2795 | +/-30% | 2032-12-01 | N/A | 1.9945 | 0 | 0 | 0 | 0 | 132kV feeder | N/A | N/A | 0 | 0 | 0 | 6917521024.6413 | 13835042049.2827 | 20752563073.924 | 27670084098.5653 | 32281764781.6596 | 32281764781.6596 | 32281764781.6596 | 41102 | 0 | 0 | 0 | 168301.3241 | 336602.6483 | 504903.9724 | 673205.2965 | 785406.1793 | 785406.1793 | 785406.1793
%Additional data includes:
- Forecast daily demand profile on maximum demand day
- Forecast daily demand profile on minimum demand day
- Connection point load duration curve
- Interval data

## System Limitations TAPR - Lines
System Limitations TAPR - Lines
Transmission line ID | Constraint primary driver | Location of constraint (start) Latitude | Location of constraint (start) Longitude | Location of constraint (end) Latitude | Location of constraint (end) Longitude | Asset rating (MVA) S25/26 or W26 | Asset rating (MVA) S26/27 or W27 | Asset rating (MVA) S27/28 or W28 | Asset rating (MVA) S28/29 or W29 | Asset rating (MVA) S29/30 or W30 | Asset rating (MVA) S30/31 or W31 | Asset rating (MVA) S31/32 or W32 | Asset rating (MVA) S32/33 or W33 | Asset rating (MVA) S33/34 or W34 | Asset rating (MVA) S34/35 or W35 | Forecast Demand P50 (MVA) S25/26 or W26 | Forecast Demand P50 (MVA) S26/27 or W27 | Forecast Demand P50 (MVA) S27/28 or W28 | Forecast Demand P50 (MVA) S28/29 or W29 | Forecast Demand P50 (MVA) S29/30 or W30 | Forecast Demand P50 (MVA) S30/31 or W31 | Forecast Demand P50 (MVA) S31/32 or W32 | Forecast Demand P50 (MVA) S32/33 or W33 | Forecast Demand P50 (MVA) S33/34 or W34 | Forecast Demand P50 (MVA) S34/35 or W35 | Forecast Demand P10 (MVA) S25/26 or W26 | Forecast Demand P10 (MVA) S26/27 or W27 | Forecast Demand P10 (MVA) S27/28 or W28 | Forecast Demand P10 (MVA) S28/29 or W29 | Forecast Demand P10 (MVA) S29/30 or W30 | Forecast Demand P10 (MVA) S30/31 or W31 | Forecast Demand P10 (MVA) S31/32 or W32 | Forecast Demand P10 (MVA) S32/33 or W33 | Forecast Demand P10 (MVA) S33/34 or W34 | Forecast Demand P10 (MVA) S34/35 or W35 | Voltage level | Maximum Load at risk per year (MVA)* S25/26 or W26 | Maximum Load at risk per year (MVA)* S26/27 or W27 | Maximum Load at risk per year (MVA)* S27/28 or W28 | Maximum Load at risk per year (MVA)* S28/29 or W29 | Maximum Load at risk per year (MVA)* S29/30 or W30 | Maximum Load at risk per year (MVA)* S30/31 or W31 | Maximum Load at risk per year (MVA)* S31/32 or W32 | Maximum Load at risk per year (MVA)* S32/33 or W33 | Maximum Load at risk per year (MVA)* S33/34 or W34 | Maximum Load at risk per year (MVA)* S34/35 or W35 | Maximum Load at risk per year (MW)* S25/26 or W26 | Maximum Load at risk per year (MW)* S26/27 or W27 | Maximum Load at risk per year (MW)* S27/28 or W28 | Maximum Load at risk per year (MW)* S28/29 or W29 | Maximum Load at risk per year (MW)* S29/30 or W30 | Maximum Load at risk per year (MW)* S30/31 or W31 | Maximum Load at risk per year (MW)* S31/32 or W32 | Maximum Load at risk per year (MW)* S32/33 or W33 | Maximum Load at risk per year (MW)* S33/34 or W34 | Maximum Load at risk per year (MW)* S34/35 or W35 | Energy at risk (MWh) S25/26 or W26 | Energy at risk (MWh) S26/27 or W27 | Energy at risk (MWh) S27/28 or W28 | Energy at risk (MWh) S28/29 or W29 | Energy at risk (MWh) S29/30 or W30 | Energy at risk (MWh) S30/31 or W31 | Energy at risk (MWh) S31/32 or W32 | Energy at risk (MWh) S32/33 or W33 | Energy at risk (MWh) S33/34 or W34 | Energy at risk (MWh) S34/35 or W35 | Preferred investment - Description | Preferred investment - Capital cost ($M REAL) | Preferred investment - Annual operating cost ($M REAL) | Preferred investment - Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Annual Deferral Value ($M REAL) | Historic line rating (MVA) S22/23 or W23 | Historic line rating (MVA) S23/24 or W24 | Historic line rating (MVA) S24/25 or W25 | Annual economic cost of constraint ($constant) S25/26 or W26 | Annual economic cost of constraint ($constant) S26/27 or W27 | Annual economic cost of constraint ($constant) S27/28 or W28 | Annual economic cost of constraint ($constant) S28/29 or W29 | Annual economic cost of constraint ($constant) S29/30 or W30 | Annual economic cost of constraint ($constant) S30/31 or W31 | Annual economic cost of constraint ($constant) S31/32 or W32 | Annual economic cost of constraint ($constant) S32/33 or W33 | Annual economic cost of constraint ($constant) S33/34 or W34 | Annual economic cost of constraint ($constant) S34/35 or W35 | VCR ($/MWh) | Annual costraint duration (hours)# | Constraint duration on peak demand day (hours)# | Project Index for interval data
Fdr 91A - Beaconsfield BSP to St Peters ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9068 | 151.1834 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 40.1759 | 40.4615 | 40.4639 | 40.8859 | 42.4438 | 42.401 | 42.3391 | 42.737 | 43.4342 | 42.4918 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.3986 | 24.8494 | 25.9732 | Replace with new 132kV feeder from Beaconsfield BSP to St Peters ZS | 22.3 | 0.0446 | 30% | 2032-12-01 | NA | 0.79566 | 97.17 | 97.17 | 97.17 | 154953.9233 | 161055.0093 | 167327.7689 | 173791.9588 | 180414.1106 | 187213.4926 | 194191.9438 | 1718488.3897 | 1819900.9446 | 1900289.5177 | 64837.627 | 0.67624 | 0.0018527 | 1
Fdr 91B - Beaconsfield BSP to St Peters ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9068 | 151.1834 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 40.2331 | 40.5035 | 40.5049 | 40.9602 | 42.4813 | 42.4394 | 42.3789 | 42.796 | 43.474 | 42.5333 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Replace with new 132kV feeder from Beaconsfield BSP to St Peters ZS | [6 empty] | 97.17 | 97.17 | 97.17 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 1
Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9118 | 151.1624 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 45.3218 | 42.4695 | 36.8152 | 35.5741 | 35.4802 | 30.5994 | 47.6856 | 46.9245 | 51.597 | 44.2597 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2586e-05 | 7.521e-05 | 8.0925e-05 | 8.5298e-05 | 8.2899e-05 | 8.5927e-05 | 8.8622e-05 | Re-arrange connections at Marrickville ZS to allow retirement of 132kV feeder 91X/1 | 1.47 | - | 30% | 2028-09-01 | 5 | 0.052449 | 99.45 | 99.45 | 99.45 | 95312.7566 | 97444.5609 | 99619.7795 | 101847.6788 | 104110.0824 | 106416.1612 | 108765.7726 | 111165.3487 | 113602.3431 | 116083.0552 | 42528 | 0.0018037 | 4.9415e-06 | 2
Fdr 91Y/1 - Beaconsfield BSP to Marrickville ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9118 | 151.1624 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 45.2029 | 42.3486 | 36.6813 | 35.4582 | 35.2584 | 30.3105 | 47.6561 | 46.8625 | 51.4756 | 44.2004 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | [9 empty] | Re-arrange connections at Marrickville ZS to allow retirement of 132kV feeder 91Y/1 | [6 empty] | 99.45 | 99.45 | 99.45 | Combined with Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | [12 empty] | 2
Fdr 91X/2 - Chullora STSS to Marrickville ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9118 | 151.1624 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 66.5289 | 64.1186 | 59.3743 | 54.3438 | 51.0023 | 40.9921 | 76.2208 | 72.4582 | 74.9824 | 73.0718 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 3.51 | - | 30% | 2028-09-01 | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 100.6 | 100.6 | 100.6 | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [12 empty] | 3
Fdr 91Y/2 - Chullora STSS to Marrickville ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9118 | 151.1624 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 68.0406 | 65.2139 | 59.8457 | 57.1727 | 54.1976 | 44.7814 | 73.3662 | 72.1949 | 76.3808 | 69.5308 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [6 empty] | 100.6 | 100.6 | 100.6 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 3
Fdr 92C - Chullora STSS to St Peters ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9068 | 151.1834 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 63.4625 | 61.1964 | 56.6252 | 51.8616 | 48.5991 | 47.4585 | 72.7434 | 69.1191 | 71.5571 | 69.8156 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 3.84 | - | 30% | 2028-09-01 |  |  | 104.03 | 104.03 | 104.03 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 4
Fdr 92X - Chullora STSS to St Peters ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9068 | 151.1834 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 67.1473 | 64.4367 | 59.1825 | 56.9584 | 53.9822 | 45.1388 | 71.7662 | 70.9161 | 75.2349 | 68.1964 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [6 empty] | 104.03 | 104.03 | 104.03 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 4
Fdr 90T/1 - Haymarket BSP to Green Square ZS | Asset condition - 132kV feeder | -33.8815 | 151.2023 | -33.9123 | 151.1945 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 139.1018 | 137.1162 | 136.7272 | 136.2 | 134.3876 | 132.9846 | 130.1411 | 127.3811 | 128.888 | 125.4158 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 6.53 | - | 30% | 1934-06-01 |  |  | 221.77 | 221.77 | 221.77 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 5
Fdr 9S2 - Beaconsfield BSP to Haymarket BSP | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.8815 | 151.2023 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 124.1417 | 122.6236 | 122.8379 | 124.1093 | 124.1482 | 124.5006 | 124.2626 | 123.9018 | 126.4625 | 123.4465 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 1.26 | - | 30% | 1934-06-01 |  |  | 225.2 | 225.2 | 225.2 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 5
Fdr 9FF - Beaconsfield BSP to Bunnerong North STS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9695 | 151.2289 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 159.0762 | 159.1713 | 151.7171 | 141.866 | 134.0774 | 130.3451 | 162.2983 | 149.9074 | 144.368 | 140.2361 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.9711 | 218.414 | 237.4307 | 257.7987 | Replace oil cable with new 132kV feeder from Beaconsfield BSP to Mill Pond Rd | 23.6 | 0.0472 | 30% | 2032-12-01 | N/A | 0.84204 | 195.48 | 195.48 | 195.48 | 189523.5069 | 198722.5975 | 208241.3035 | 217052.8046 | 227175.5967 | 237629.6706 | 7316776.0844 | 9236833.1906 | 10029931.7619 | 10878922.1993 | 41102 | 0.98645 | 0.0027026 | 6
Fdr 9SE - Beaconsfield BSP to Green Square ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9123 | 151.1945 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 113.2923 | 116.4032 | 123.6187 | 150.5208 | 177.1427 | 203.696 | 254.2552 | 287.7233 | 317.0927 | 311.321 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62433 | 0.66618 | 0.74032 | 0.84354 | 0.88924 | 0.92069 | 0.94525 | 0.95173 | 0.95907 | 0.97898 | Replace with new 132kV feeder from Beaconsfield BSP to Green Square ZS | 7.5 | 0.015 | 30% | 2034-06-01 | 2 | 0.2676 | 225.2 | 225.2 | 225.2 | 35797.5789 | 37724.3544 | 40985.2013 | 45448.4105 | 47553.765 | 49080.2532 | 50330.0907 | 50844.4932 | 51400.4174 | 52479.5708 | 41102 | 0.22368 | 0.00061283 | 7
Fdr 270 - Kingsford ZS to Maroubra ZS | Asset condition - 132kV feeder | -33.927248 | 151.23 | -33.9422 | 151.238 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 88.2031 | 85.5956 | 83.3653 | 83.2858 | 82.5652 | 81.6798 | 90.0407 | 81.4782 | 84.2887 | 81.0496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.237 | 1.4304 | 1.5847 | 1.7521 | 2.0179 | 2.2626 | 2.4756 | 2.6192 | 2.8321 | 3.0881 | Replace with two new 132kV feeders (Bunnerong STSS - Kingsford ZS, Maroubra ZS - Clovelly ZS) and decommission 132kV feeder 262 | 10.1 | 0.0202 | 30% | 1934-06-01 | N/A | 0.36037 | 225.2 | 225.2 | 225.2 | 161588.9819 | 173019.6762 | 183009.4058 | 193652.3919 | 208325.3787 | 222278.8194 | 235089.868 | 245274.2177 | 258334.0519 | 273235.1777 | 39861 | 0.22668 | 0.00062104 | 8
*Maximum load at risk is provided for credible contingencies and only assumes committed projects
#Constraint duration provided for year of proposed timing of preferred investment