## AG2023 - Final
Location | Feeder Name | Type of risk | Rating | Summer 22/23 load (11kV amps) | Forecast Summer 23/24 (% over threshold) | Forecast Summer 24/25 (% over threshold) | Forecast Summer 25/26 (% over threshold) | Winter 2023 load (11kV amps) | Forecast Winter 2024 (% over threshold) | Forecast Winter 2025 (% over threshold) | Forecast Winter 2026 (% over threshold) | Reduction Required (MVA) | Potential Solution
Sydney CBD | Dalley ST 33 KLM | N | 600. Reduces to 0 in 2024/25 with Dalley St ZS decom. | 206 | 0% | 100% | 100% | 264 | 0% | 100% | 100% | 3.9615 | Project under construction, eta 2024
Gillieston Heights | Telarah PA10 | N | 315 | 260 | 16% | 21% | 26% | 167 | 0% | 0% | 0% | 1.1712 | Project issued 2022
Rutherford/Lochivar | Rutherford PA14 | N | 400 | 300 | 18% | 38% | 58% | 239 | 16.36% | 34.55% | 50.91% | 1.8488 | Project issued 2023
Gillieston Heights | Metford PA13 | N-1 | 330 | 160 | 70% | 76% | 82% | 102 | 0% | 0% | 0% | 2.1192 | Project issued 2022
Gillieston Heights | Metford PA10 | N-1 | 315 | 275 | 68% | 70% | 72% | 164 | 0% | 0% | 0% | 3.1635 | Project issued 2022
Gillieston Heights | Kurri PA19 | N-1 | 400 | 289 | 76% | 80% | 84% | 181 | 0% | 0% | 0% | 4.0385 | Project issued 2022
Breakfast Point | Concord PA4 | N-1 | 320 | 300 | 80.33% | 80.33% | 80.33% | 190 | 0% | 0% | 0% | 4.6346 | Project issued 2022
Breakfast Point | Concord PA7 | N-1 | 305 | 160 | 70% | 70% | 70% | 140 | 0% | 0% | 0% | 2.1538 | Project issued 2022
Breakfast Point | Concord PA15 | N-1 | 310 | 190 | 85.26% | 85.26% | 85.26% | 100 | 0% | 0% | 0% | 3.1154 | Project issued 2022
Breakfast Point | Concord PA17 | N-1 | 315 | 200 | 75.5% | 75.5% | 75.5% | 180 | 0% | 0% | 0% | 2.9038 | Project issued 2022
Breakfast Point | Concord PA18 | N-1 | 315 | 275 | 77.09% | 77.09% | 77.09% | 200 | 0% | 0% | 0% | 4.0769 | Project issued 2022
Breakfast Point | Concord PA22 | N-1 | 315 | 315 | 67.94% | 67.94% | 67.94% | 230 | 0% | 0% | 0% | 4.1154 | Project issued 2022
Breakfast Point | Burwood PA21 | N-1 | 240 | 240 | 22.92% | 22.92% | 22.92% | 225 | 0% | 0% | 0% | 1.0577 | Project issued 2022
Avoca | Avoca PA37 | N-1 | 320 | 184 | 47.67% | 47.76% | 47.76% | 178 | 50.05% | 50.15% | 50.15% | 1.837 | Under investigation
Somersby | Somersby PA17 | N-1 | 295 | 124 | 36% | 36% | 36% | 126 | 29% | 29% | 29% | 1.08 | Project issued 2023
Branxton | Branxton 66 PA17 (83743) | N-1 | 300 | 236 | 16.59% | 16.72% | 17% | 157 | 9.842% | 9.921% | 10% | 0.77489 | Under investigation
Cessnock | Cessnock South PA 2 | N-1 | 324 | 233 | 14.86% | 14.92% | 14.92% | 174 | 9.769% | 9.808% | 10% | 0.73718 | Under investigation
Killarney | Killarney PA 2 | N-1 | 320 | 213 | 8.563% | 8.563% | 8.563% | 190 | 9.465% | 9.465% | 9.465% | 0.31289 | Under investigation
Matraville | Matraville PA43 | N-1 | 400 | 119 | 1% | 1% | 1% | 127 | 0% | 0% | 0% | 0.1 | Under investigation
Muswellbrook | Muswellbrook 33 PA 3 (74121) | N-1 | 319 | 80 | 16.85% | 17.04% | 17% | 78 | 16.64% | 16.82% | 17% | 0.25882 | Under investigation
Singleton | Singleton 66 PA28 (83500) | N-1 | 450 | 192 | 87.39% | 87.39% | 87% | 184 | 83.75% | 83.75% | 84% | 3.2266 | Under investigation
Tighes Hill | Tighes Hill PA12 | N-1 | 422 | 158 | 6.099% | 6.105% | 6% | 134 | 4.548% | 4.553% | 5%% | 0.20312 | Under investigation
Aberglassyn | Maitland PA07 | N-1 | 290 | 284 | 62% | 78% | 93.95% | 180 | 0% | 0% | 0% | 5.03 | Under investigation
Bolwarra | Maitland PA13 | N-1 | 260 | 216 | 66% | 67% | 68.24% | 148 | 0% | 0% | 0% | 3 | Under investigation
Aberglassyn | Maitland PA04 | N-1 | 260 | 223 | 66% | 82% | 99.16% | 138 | 0% | 0% | 0% | 4.47 | Under investigation
Largs | Maitland PA11 | N-1 | 260 | 257 | 80% | 86% | 92.89% | 156 | 0% | 0% | 0% | 4.47 | Under investigation
Aberglassyn | Rutherford PA02 | N | 350 | 337 | 24% | 30% | 37.31% | 213 | 0% | 0% | 0% | 2.74 | Under investigation
Aberglassyn | Rutherford PA09 | N-1 | 350 | 143 | 34.97% | 52% | 82.53% | 96 | 0% | 0% | 0% | 2.5385 | Under investigation
Aberglassyn | Telarah PA08 | N-1 | 295 | 240 | 82% | 91% | 100% | 157 | 0% | 0% | 0% | 4.6923 | Under investigation
Maroubra | Maroubra PA35 | N-1 | 305 | 160 | 12% | 12% | 12 | 140 | 0% | 0% | 0% | 0.7 | Under Investigation
Avondale | Avondale fdr 13020 | N | 293 | 115 | 1% | 1% | 1 | 83 | 0% | 0% | 0% | 0.56 | Under Investigation
Morisset | Morisset fdr 80075 | N | 364 | 205 | 24% | 24% | 24 | 200 | 0% | 0% | 0% | 1.66 | Under Investigation
St Peters | St Peters PA14R | N-1 | 391 | 290 | 40% | 40% | 40% | 197 | 0 | 0 | 0 | 1.9 | Under Investigation
Note on M1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use nominal volts